## 1
Toase-ehe Park Sanati Gohar Ofogh Petrochemical Co. CONCEPTUAL, BASIC and DETAIL DESIGN ENGINEERING OF STYRENE PARK OFFSITE
#REF!
|  |  | #REF! | [13 empty] | #REF! |  | Page 3 of 3
ITEM | REV. | TAG NO. | Description | Load Type | Load Statude | Operating Type | Voltage Type | Voltage (V) | Frequency (Hz) | Mechanical Absorbed Power (KW) | Rotor Shaft Power @Min Temp | API 661 Factor (part: 7.2.7.1.2 | Absorbed Power (KW) (see note 1) | EFF. | P.F. | Operating Power(Kw | Rated Power | rated Current | Density Factor | Starting Method
1 | 0 | RU0001A-M-03 | Air cooler MOTOR LOAD LV-400V | M | C | N | 3 PH | 400±5% | 50±2% | 4.5 | 5.3 | 1.05 | 4.9737 | 0.9 | 0.84 | 6.9 | 7.5 | 14.43 | 1 | VFD
2 | 0 | RU0001A-M-02 | Air cooler MOTOR LOAD LV-400V | M | C | N | 3 PH | 400±5% | 50±2% | 4.5 | 5.3 | 1.05 | 4.9737 | 0.9 | 0.84 | 6.9 | 7.5 | 14.43 | 1 | DOL
3 | 0 | RU0001B-M-03 | Air cooler MOTOR LOAD LV-400V | M | C | N | 3 PH | 400±5% | 50±2% | 4.5 | 5.3 | 1.05 | 4.9737 | 0.9 | 0.84 | 6.9 | 7.5 | 14.43 | 1 | VFD
4 | 0 | RU0001B-M-02 | Air cooler MOTOR LOAD LV-400V | M | C | N | 3 PH | 400±5% | 50±2% | 4.5 | 5.3 | 1.05 | 4.9737 | 0.9 | 0.84 | 6.9 | 7.5 | 14.43 | 1 | DOL
C: Countinus Operation
CS: Countinus Standby
IO: Intermitant Operation
SD: Shutdown operation
SU: Start Up operation
N: Normal Load
E:Emergency Load
DOL: Direct on Line Staring
VFD: Variable Frequency Drive