| DEFINITIONS: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| COLUMN POWER SUPPLY : |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | "STATUS SUPPLY" INDICATES TYPE OF POWER SUPPLY |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | N | : NORMAL |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | E | : EMERGENCY |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | U | : UPS LOADS |  |  |  |  |  |  |  |  |  |  |  |  |  |
| COLUMN RATED POWER (KW) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | RATED POWER SHALL BE CONSIDERED MECHANICAL POWER WITH API FACTOR CONSIDERATION AND |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | NORMALIZATION TO STANDARD RATING POWERS (REFER TO IEC60072-1) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| COLUMN EFFICIENCY (%) : |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | EFFICIENCY FACTOR AT NORMAL LOAD |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| COLUMN POWER FACTOR (%) : |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | POWER FACTOR AT NORMAL LOAD |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| REV. |  | ITEM | TAG NO. | Description | Quantity Total | Quantity |  |  | Rated Power (KW) | Normal Power (KW) | Rated Voltage | Efficiency (%) | Power Factor | 3 phase / 1 phase | Power Supply | REMARKS |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | Continuous | Intermittent | Standby |  |  |  |  |  |  | N/E/U |  |  |
| 0 |  | 1 | 70-UCP-RU7001A/B | Unit Control Panel | 1 | x | - | - | 2.500 | 2.500 | 110 VAC | 100 | 0.97 | 1 phase | U |  |  |
| 0 |  | 2 | 70-UCP-RU7001A/B | Unit Control Panel | 1 | x | - | - | 1.000 | 1.000 | 220 VAC | 100 | 0.97 | 1 phase | N |  |  |
| 0 |  | 3 | RU0001A-M-01 | Main Motor | 1 | x | - | - | 120 | 120 | 400 VAC | 95.4 | 0.91 | 3 phase | N |  |  |
| 0 |  | 4 | RU0001B-M-01 | Main Motor | 1 | x | - | - | 120 | 120 | 400 VAC | 95.4 | 0.91 | 3 phase | N |  |  |
| 0 |  | 5 | RU0001A-MSH-01 | Main Motor Space Heater | 1 | - | x | - | 0.109 | 0.109 | 230AC | 100 | 1.00 | 1 phase | N |  |  |
| 0 |  | 6 | RU0001B-MSH-01 | Main Motor Space Heater | 1 | - | x | - | 0.109 | 0.109 | 230AC | 100 | 1.00 | 1 phase | N |  |  |
| 0 |  | 7 | RU0001A-M-04 | AUX Motor | 1 | x | - | - | 2.5 | 2.5 | 400VAC | 87.7 | 0.8 | 3 phase | N |  |  |
| 0 |  | 8 | B-M-04 | AUX Motor | 1 | x | - | - | 2.5 | 2.5 | 400VAC | 87.7 | 0.8 | 3 phase | N |  |  |
| 0 |  | 9 | RU0001A-H-01 | Oil Heater | 1 | x | - | - | 2 | 2 | 400VAC | 100 | 1 | 3 phase | N |  |  |
| 0 |  | 10 | RU0001B-H-01 | Oil Heater | 1 | x | - | - | 2 | 2 | 400VAC | 100 | 1 | 3 phase | N |  |  |