| INSTRUMENT AIR |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ITEM | SERVICE | FLUID (PHASE) | PIPING SIZE | FLOW (Nm3/h) Cont. / Design | TEMPERATURE (°C) |  |  |  | PRESSURE (barg) |  |  |  | DURATION |
|  |  |  |  |  | MIN. | NORM. | MAX. | DESIGN | MIN. | NORM. | MAX. | DESIGN |  |
| REFRIGERATION PACKAGE RU0001 A/B | VALVES | INSTRUMENT AIR (GAS) | 1/2" | 1.8 / - | 5 | AMB. | 50 | 85 | 6.5 | 7 | 7.5 | 10.5 | CONTINUOUS |
| NOTES: 1) Air Consumption for Control Valves= 0.9 Nm3/h Per Valve. |  |  |  |  |  |  |  |  |  |  |  |  |  |

GENARL NOTES:

1) Utility consumption data are considered for whole package.

| DEFINITIONS: |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COLUMN POWER SUPPLY : |  |  |  |  |  |
|  | "STATUS SUPPLY" INDICATES TYPE OF POWER SUPPLY |  |  |  |  |  |
|  | N | : NORMAL |  |  |  |  |
|  | E | : EMERGENCY |  |  |  |  |
|  | U | : UPS LOADS |  |  |  |  |
| COLUMN RATED POWER (KW) |  |  |  |  |  |
|  | RATED POWER SHALL BE CONSIDERED MECHANICAL POWER WITH API FACTOR CONSIDERATION AND |  |  |  |  |  |
|  | NORMALIZATION TO STANDARD RATING POWERS (REFER TO IEC60072-1) |  |  |  |  |  |
| COLUMN EFFICIENCY (%) : |  |  |  |  |  |
|  | EFFICIENCY FACTOR AT NORMAL LOAD |  |  |  |  |
| COLUMN POWER FACTOR (%) : |  |  |  |  |  |
|  | POWER FACTOR AT NORMAL LOAD |  |  |  |  |

| REV. | ITEM | TAG NO. |  |  | Description |  | Quantity Total | Quantity |  |  |  |  |  | Rated Power (KW) |  | Normal Power (KW) |  | Rated Voltage |  | Efficiency (%) |  | Power Factor | 3 phase / 1 phase |  | Power Supply |  | REMARKS |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  | Continuous |  | Intermittent |  | Standby |  |  |  |  |  |  |  |  |  |  |  |  | N/E/U |  |  |  |  |  |
| 0 | 1 | 70-UCP-RU7001A/B |  |  | Unit Control Panel |  | 1 | x |  | - |  | - |  | 2.500 |  | 2.500 |  | 110 VAC |  | 100 |  | 0.97 | 1 phase |  | U |  |  |  |  |  |
| 0 | 2 | 70-UCP-RU7001A/B |  |  | Unit Control Panel |  | 1 | x |  | - |  | - |  | 1.000 |  | 1.000 |  | 220 VAC |  | 100 |  | 0.97 | 1 phase |  | N |  |  |  |  |  |
| 0 | 3 | RU0001A-M-01 |  |  | Main Motor |  | 1 | x |  | - |  | - |  | 120 |  | 120 |  | 400 VAC |  | 95.4 |  | 0.91 | 3 phase |  | N |  |  |  |  |  |
| 0 | 4 | RU0001B-M-01 |  |  | Main Motor |  | 1 | x |  | - |  | - |  | 120 |  | 120 |  | 400 VAC |  | 95.4 |  | 0.91 | 3 phase |  | N |  |  |  |  |  |
| 0 | 5 | RU0001A-MSH-01 |  |  | Main Motor Space Heater |  | 1 | - |  | x |  | - |  | 0.109 |  | 0.109 |  | 230AC |  | 100 |  | 1.00 | 1 phase |  | N |  |  |  |  |  |
| 0 | 6 | RU0001B-MSH-01 |  |  | Main Motor Space Heater |  | 1 | - |  | x |  | - |  | 0.109 |  | 0.109 |  | 230AC |  | 100 |  | 1.00 | 1 phase |  | N |  |  |  |  |  |
| 0 | 7 | RU0001A-M-04 |  |  | AUX Motor |  | 1 | x |  | - |  | - |  | 2.5 |  | 2.5 |  | 400VAC |  | 87.7 |  | 0.8 | 3 phase |  | N |  |  |  |  |  |
| 0 | 8 | B-M-04 |  |  | AUX Motor |  | 1 | x |  | - |  | - |  | 2.5 |  | 2.5 |  | 400VAC |  | 87.7 |  | 0.8 | 3 phase |  | N |  |  |  |  |  |
| 0 | 9 | RU0001A-H-01 |  |  | Oil Heater |  | 1 | x |  | - |  | - |  | 2 |  | 2 |  | 400VAC |  | 100 |  | 1 | 3 phase |  | N |  |  |  |  |  |
| 0 | 10 | RU0001B-H-01 |  |  | Oil Heater |  | 1 | x |  | - |  | - |  | 2 |  | 2 |  | 400VAC |  | 100 |  | 1 | 3 phase |  | N |  |  |  |  |  |

| ITEM | REV. | TAG NO. | Description | Load Type |  | Load Statude |  | Operating Type |  | Voltage Type |  | Voltage (V) |  | Frequency (Hz) |  | Mechanical Absorbed Power (KW) |  | Rotor Shaft Power @Min Temp |  | API 661 Factor (part: 7.2.7.1.2 |  | Absorbed Power (KW) (see note 1) |  | EFF. |  | P.F. |  | Operating Power(Kw |  | Rated Power |  | rated Current |  | Density Factor |  | Starting Method |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 0 | RU0001A-M-03 | Air cooler MOTOR LOAD LV-400V | M |  | C |  | N |  | 3 PH |  | 400±5% |  | 50±2% |  | 4.5 |  | 5.3 |  | 1.05 |  | 4.97 |  | 0.9 |  | 0.84 |  | 6.9 |  | 7.5 |  | 14.43 |  | 1 |  | VFD |  |
| 2 | 0 | RU0001A-M-02 | Air cooler MOTOR LOAD LV-400V | M |  | C |  | N |  | 3 PH |  | 400±5% |  | 50±2% |  | 4.5 |  | 5.3 |  | 1.05 |  | 4.97 |  | 0.9 |  | 0.84 |  | 6.9 |  | 7.5 |  | 14.43 |  | 1 |  | DOL |  |
| 3 | 0 | RU0001B-M-03 | Air cooler MOTOR LOAD LV-400V | M |  | C |  | N |  | 3 PH |  | 400±5% |  | 50±2% |  | 4.5 |  | 5.3 |  | 1.05 |  | 4.97 |  | 0.9 |  | 0.84 |  | 6.9 |  | 7.5 |  | 14.43 |  | 1 |  | VFD |  |
| 4 | 0 | RU0001B-M-02 | Air cooler MOTOR LOAD LV-400V | M |  | C |  | N |  | 3 PH |  | 400±5% |  | 50±2% |  | 4.5 |  | 5.3 |  | 1.05 |  | 4.97 |  | 0.9 |  | 0.84 |  | 6.9 |  | 7.5 |  | 14.43 |  | 1 |  | DOL |  |
| C: Countinus Operation |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| CS: Countinus Standby |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| IO: Intermitant Operation |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| SD: Shutdown operation |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| SU: Start Up operation |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| N: Normal Load |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| E:Emergency Load |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| DOL: Direct on Line Staring |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| VFD: Variable Frequency Drive |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |