## Table 1
Toase-ehe Park Sanati Gohar Ofogh Petrochemical Co. CONCEPTUAL, BASIC and DETAIL DESIGN ENGINEERING OF STYRENE PARK OFFSITE
|  | Project: Refrigeration System Styrene Park Joint Facility Project (Offsite) | Vendor Title: Inspection And Test (ITP) |  |  | CLIENT/OWNER: PETRO ELECTRIC/GOHAR OFOGH
|  | VENDOR NAME: DELTA GMBH | VENDOR DOC. NO.: EI027-HSE-VD-QC-ITP-001- R0
QUALITY CONTROL / INSPECTION & TEST PLAN (ITP) FOR REFRIGERATION UNIT
1 | SCOPE | This Inspection and Test plan covers all activtiies that will be carrived out in design and farbrication of equipment. | [8 empty] | DATE: 17.Sep.2023
2 | LEGEND OF THE TECHNICAL SURVEILLANCE | 1) (H)= INSPECTION NOTIFICATION will be issued by manufacturer and inspection shall be performed at presence of notified party. Next farbication stage is subject to acceptance of inspection. Vendor must notify parties (see inspection activtiy) of the defidcated inspection activity at least fifteen (15) days in advance. | [8 empty] | REV.: R0
|  | 2) (SW)=10% OF TYPE/LOT WITNESSED. Action performed only on a certain number of pieces. | [8 empty] | BY : AM
3) (W)=WITNESSING. The Supplier shall inform the NOTIFIED PARTY of the date of the activity and the NOTIFIED PARTY reserves the right to witness the test. If the test is conducted at the notified date, the Supplier may proceed with the subsequent phase, even if the NOTIFIED did not witness the test.
4) (R/A)=REVIEW OF TECHNICAL DOCUMENTS BEFORE COMMENCEMENT OF CONSTRUCTION. The technical documents shall be reviewed and approved before the commencement of construction
5) (R )=REVIEW OF DOCUMENTS. Materials certificates, statement of compliance and reports of inspection and tests conducted by the Supplier shall be revised to assess their conformance with the requirements specified in the Code and Standards, Specifications and/or Purchase Order.
6) (D) = Vendor Inspection
3 | Abbreviations | O = Owner (GOPC) V = Vendor SV = Sub Vendor TPI = Third Party Inspection on behalf of owner
Item No. | Inspection Description | References / Specifications / Codes | Verifying Document | Acceptance Criteria |  | INSPECTION ACTIVITY
[11 empty] | REMARKS | R E V
[6 empty] | SUB-VENDOR(SV) | VENDOR(V) | PE | Client/TPI
A PROJECT PREPARATION
A1 | Submission of Project documents |  |  |  | TYPE | H | H | R | R
DATE
SIGN
A2 | PRE INSPECTION MEETING |  |  |  | TYPE | H | H | H | H | -
DATE
SIGN
A3 | BASIC DESIGN DRAFT DOCUMENT LIST P&ID , LAY-OUT |  |  |  | TYPE | H | H | R | R | -
DATE
SIGN
A4 | KICK-OFF MEETING CUSTOMER DETAILLED DESIGN |  |  |  | TYPE | H | H | R | R | -
DATE
SIGN
B MATERIAL SELECTION / SUBCONTRACTOR ORDERING
B0 | GENERAL | ALL ITEMS SUITABLE FOR AMBIENT TEMPERATURE | MATERIAL SUPPLY |  | TYPE | H | H | R | R | -
|  |  | FABRICATION SCHEDULE |  | DATE
|  |  | QA / QC |  | SIGN
B1 | COMPRESSOR Block | MYCOM STANDARD Procedures | TEST REPORT For Compressor: '- Noise test '- Vibration test '- Perfromance test '- Running test '-Hydro test | MATERIAL CERTIFICATES | TYPE | H | R | R | R | -
| MAYEKAWA(MYCOM) |  |  |  | DATE
SIGN
B2 | MAIN MOTOR - HELMKE/Schorch GERMANY | As Per HELMKE GERMANY Test Procedures | TEST REPORT ( Manuf. Std ) |  | TYPE | H | H | R | R | -
|  | Hazardous Area Certificates | - Unwitenssed routine test report |  | DATE
|  | Ex ec |  |  | SIGN
B3 | Compressor Skids including Oil pump, Oil Filter, Piping, Oil Separator, etc | MYCOM MANUFACTURER STANDARD Test Procedure and Quality Control | TEST REPORT | MATERIAL CERTIFICATES | TYPE | H | H | R | R | -
DATE
SIGN
B4 | PUMP MOTOR-HELMKE/Schorch GERMANY | MANUFACTURER STANDARD with protection class as per Exec | TEST REPORT ( Manuf. Std ) |  | TYPE | H | H | R | R | -
|  | HAZARDOUS AREA CERTIFICATE | - Unwitenssed routine test report |  | DATE
|  | Ex ec |  |  | SIGN
NOTE : CERTIFIED COMPLETE: ENDORSEMENTS:

## Table 2
Toase-ehe Park Sanati Gohar Ofogh Petrochemical Co. CONCEPTUAL, BASIC and DETAIL DESIGN ENGINEERING OF STYRENE PARK OFFSITE
|  | Project: Refrigeration System Styrene Park Joint Facility Project (Offsite) | Vendor Title: Inspection And Test (ITP) |  |  | CLIENT/OWNER: PETRO ELECTRIC/GOHAR OFOGH
|  | VENDOR NAME: DELTA GMBH | VENDOR DOC. NO.: EI027-HSE-VD-QC-ITP-001-R0
QUALITY CONTROL / INSPECTION & TEST PLAN (ITP) FOR REFRIGERATION UNIT
1 | SCOPE | This Inspection and Test plan covers all activtiies that will be carrived out in design and farbrication of equipment. | [8 empty] | DATE: 17.Sep.2023
2 | LEGEND OF THE TECHNICAL SURVEILLANCE | 1) (H)= INSPECTION NOTIFICATION will be issued by manufacturer and inspection shall be performed at presence of notified party. Next farbication stage is subject to acceptance of inspection. Vendor must notify parties (see inspection activtiy) of the defidcated inspection activity at least fifteen (15) days in advance. | [8 empty] | REV.:R0
|  | 2) (SW)=10% OF TYPE/LOT WITNESSED. Action performed only on a certain number of pieces. | [8 empty] | BY : AM
3) (W)=WITNESSING. The Supplier shall inform the NOTIFIED PARTY of the date of the activity and the NOTIFIED PARTY reserves the right to witness the test. If the test is conducted at the notified date, the Supplier may proceed with the subsequent phase, even if the NOTIFIED did not witness the test.
4) (R/A)=REVIEW OF TECHNICAL DOCUMENTS BEFORE COMMENCEMENT OF CONSTRUCTION. The technical documents shall be reviewed and approved before the commencement of construction
5) (R )=REVIEW OF DOCUMENTS. Materials certificates, statement of compliance and reports of inspection and tests conducted by the Supplier shall be revised to assess their conformance with the requirements specified in the Code and Standards, Specifications and/or Purchase Order.
6) (D) = Vendor Inspection
3 | Abbreviations | O = Owner (GOPC) V = Vendor SV = Sub Vendor TPI = Third Party Inspection on behalf of owner
Item No. | Inspection Description | References / Specifications / Codes | Verifying Document | Acceptance Criteria |  | ATTENDED BY |  |  |  |  | REMARKS
[6 empty] | SUB-VENDOR(SV) | VENDOR(V) | PE | Client/TPI
B MATERIAL SELECTION / SUBCONTRACTOR ORDERING (CONTINUE)
B5 | HEAT EXCHANGERS | ASME VIII DIV 1 | MATERIAL CERTIFICATES 3.1 FOR PRESSURE RETAINING PARTS 2.2 WELD FILLER AND NON PRESSURE RETAINING PARTS | MANUFACTURING STANDARD & Approved Drawing | TYPE | H | W | R | R
DATE
SIGN
| PROPANE CONDENSOR / CHILLER | ASME Sec. VIII Div. 1 and TEMA | WPS/PQR – WELDER QUALIFICATIONS WELD - WELDING CHECK NDE REPORTS CLEANLINESS TREATMENT HYDRAULIC & PRESSURE STATIC TEST DIMENSIONAL INSPECTION RT/UT REQUIREMENT Spot (on pressure retaining parts) PAINTING INSPECTION |  | TYPE | H | W | R | R
DATE
SIGN
B6 | BASE FRAME For CHILLER |  | PT -10 % OF MAJOR STRUCTURAL CONNECTIONS 100 % PT LIFTING LUG WELDS 100 % UT BUTT WELDS IN MAJOR SUPPORTING BEAMS | ACC. Vendor DATASHEET/DRAWING SKID CONNECTION POINTS – ANCHOR BOLT POSITIONS INSPECTION /CERTIFICATE | TYPE | H | H | R | R | -
DATE
SIGN
B7 | VALVES | ASME/MYCOM STD For Compressor skid | MANUFACTURER INSPECTION AND TEST RECORD | ACC. Vendor DATASHEET/DRAWING INSPECTION /CERTIFICATE | TYPE | H | W | R | R |  | Inspection will be at Vendor workshop
DATE
SIGN
B8 | PIPING | ASME/MYCOM STD For Compressor skid | 1) Carbon oil and refrigerant piping 10% . 2) Instrument air header 10% . Amount will be based on total amount of welded inches. | Material certificates | TYPE | H | W | R | R | -
DATE
SIGN
B9 | SAFETY VALVES |  | MATERIAL CERTIFICATES 3.1 TEST REPORT | INSPECTION | TYPE | H | W | R | R
|  | ASME/MYCOM STD For Compressor skid |  | REPORT | DATE
SIGN
B10 | Smaller components within instrumenetation routing, such asTUBING and GASKETS and bolting . |  | MATERIAL CERTIFICATES 3.1 | INSPECTION | TYPE | H | R | R | R
|  |  |  | CERTIFICATE | DATE
SIGN
B11 | INSTRUMENTATION | Pressure and temperature guages are provided with 3.1 material certificates | MATERIAL CERTIFICATES 3.1 DIMENSIONAL AND CONSTRUCTION DWG HAZARDOUS AREA CERTIFICATE CALIBRATION REPORT (3.1 material certificates). 3 point calibration |  | TYPE | H | R | R | R
DATE
SIGN
NOTE : CERTIFIED COMPLETE: ENDORSEMENTS:

## Table 3
Toase-ehe Park Sanati Gohar Ofogh Petrochemical Co. CONCEPTUAL, BASIC and DETAIL DESIGN ENGINEERING OF STYRENE PARK OFFSITE
|  | Project: Refrigeration System Styrene Park Joint Facility Project (Offsite) | Vendor Title: Inspection And Test (ITP) |  |  | CLIENT/OWNER: PETRO ELECTRIC/GOHAR OFOGH
|  | VENDOR NAME: DELTA GMBH | VENDOR DOC. NO.: EI027-HSE-VD-QC-ITP-001- R0
QUALITY CONTROL / INSPECTION & TEST PLAN (ITP) FOR REFRIGERATION UNIT
1 | SCOPE | This Inspection and Test plan covers all activtiies that will be carrived out in design and farbrication of equipment. | [7 empty] | DATE: 17.Sep.2023
2 | LEGEND OF THE TECHNICAL SURVEILLANCE | 1) (H)= INSPECTION NOTIFICATION will be issued by manufacturer and inspection shall be performed at presence of notified party. Next farbication stage is subject to acceptance of inspection. Vendor must notify parties (see inspection activtiy) of the defidcated inspection activity at least fifteen (15) days in advance. | [7 empty] | REV.: 00
|  | 2) (SW)=10% OF TYPE/LOT WITNESSED. Action performed only on a certain number of pieces. | [7 empty] | BY : AM
3) (W)=WITNESSING. The Supplier shall inform the NOTIFIED PARTY of the date of the activity and the NOTIFIED PARTY reserves the right to witness the test. If the test is conducted at the notified date, the Supplier may proceed with the subsequent phase, even if the NOTIFIED did not witness the test.
4) (R/A)=REVIEW OF TECHNICAL DOCUMENTS BEFORE COMMENCEMENT OF CONSTRUCTION. The technical documents shall be reviewed and approved before the commencement of construction
5) (R )=REVIEW OF DOCUMENTS. Materials certificates, statement of compliance and reports of inspection and tests conducted by the Supplier shall be revised to assess their conformance with the requirements specified in the Code and Standards, Specifications and/or Purchase Order.
6) (D) = Vendor Inspection
3 | Abbreviations | O = Owner (GOPC) V = Vendor SV = Sub Vendor TPI = Third Party Inspection on behalf of owner
Item No. | Inspection Description | References / Specifications / Codes | Verifying Document | Acceptance Criteria |  | ATTENDED BY |  |  |  | REMARKS
[6 empty] | SUB-VENDOR(SV) | VENDOR(V) | PE | Client/TPI
C INSPECTION
C1 | DIMENSIONAL INSPECTION OF SKID CONNECTION POINTS |  |  |  | TYPE | H | SW | R | R | Timer period of PMI will be informed.No specific dates are consider to be informed in advance by Vendor
DATE
SIGN
C2 | PAINTING | Vendor STANDARD / SUPPLIER_(Painting_Standard) | THICKNESS VISUAL INSPECTION and measurement via instrument. PAINT INSPECTION REPORT |  | TYPE | H | W | R | R
[5 empty] | DATE |  | - | - | -
SIGN
C3 | ELECTRICAL WIRING | WIRING CHECK |  |  | TYPE | H | W | R | R
DATE
SIGN
C4 | INSPECTION OF JUCTION BOX, LOCAL PANEL AND PLC | FACTORY ACCEPTANCE TEST FOR PLC 1) VISUAL INSPECTION JUNCTION BOX, LOCAL PANEL AND PLC 2) FUNCTION TEST | TEST REPORT PLC FAT TEST PROCEDURE | CONTROL NARRATIVE DRAWINGS, DATA SHEETS | TYPE | H | W | W | W
DATE
SIGN
C5 | RUST PREVENTION FOR STORAGE | Vendor STANDARD | NITROGEN CHARGING -0.5 BAR |  | TYPE | H | W | R | R
DATE
SIGN
C6 | FINAL INSPECTION |  | NAME PLATES CONFIRMATION | RELEASE NOTE | TYPE | H | H | W | W
DATE
SIGN
C7 | APPROVAL OF CONCESSION REQUEST AND NON-CONFORMANCE REPORTS |  |  |  | TYPE | H | R | R / A | R / A
DATE
SIGN
D SHIPMENT AND LOADING
D1 | PACKING AND MARKING PREPARATION FOR SHIPMENT DETAILED PACKING LIST AND LOOSE DELIVERY LIST | Shrinked Packed | PACKING INSPECTION: VISUAL INSPECTION COMPLETENESS CHECK PACKING LIST |  | TYPE | H | R | R | R
DATE
SIGN
D2 | DOCUMENTATION | As per Agreed document List | A COMPLETE PACKAGE OF INSPECTION AND TEST RECORD/CERTIFICATE MANUFACTURED RECORD |  | TYPE | H | R/A | R/A | R/A
|  | Incl. Final data book, ITP, etc. |  |  | DATE
SIGN
NOTE : CERTIFIED COMPLETE: ENDORSEMENTS: