## Modbus RTU
Name |  | Type | Offset | Register | Decimal
Read | [5 empty] | MODBUS RTU slave settings (default)
Analog inputs | [5 empty] | Modbus slave address: 1
Compressor package A (RU0001A) | [5 empty] | Baud rate: 19200
PS | BarG | Int | 0 | 40000 | x100 | Parity: 2
PD | BarG | Int | 2 | 40001 | x100 | Half duplex(RS485) 2-wire operation
POH | BarG | Int | 4 | 40002 | x100
POS | BarG | Int | 6 | 40003 | x100
PBOF | BarG | Int | 8 | 40004 | x100
PAOF | BarG | Int | 10 | 40005 | x100
TS | °C | Int | 12 | 40006 | x100
TD | °C | Int | 14 | 40007 | x100
TOH | °C | Int | 16 | 40008 | x100
MA | A | Int | 18 | 40009 | x100
CAP_% | % | Int | 20 | 40010 | x100
DOP | Bar | Int | 22 | 40011 | x100
DOF | Bar | Int | 24 | 40012 | x100
DFF | Bar | Int | 26 | 40013 | x100
Spare |  | Int | 28 | 40014 | x100
Spare |  | Int | 30 | 40015 | x100
Spare |  | Int | 32 | 40016 | x100
Spare |  | Int | 34 | 40017 | x100
DOS | Bar | Int | 36 | 40018 | x100
LCHILL | % | Int | 38 | 40019 | x100
Spare30 |  | Int | 40 | 40020 | x100
Spare31 |  | Int | 42 | 40021 | x100
Spare32 |  | Int | 44 | 40022 | x100
Compressor package B (RU0001B)
PS | BarG | Int | 46 | 40023 | x100
PD | BarG | Int | 48 | 40024 | x100
POH | BarG | Int | 50 | 40025 | x100
POS | BarG | Int | 52 | 40026 | x100
PBOF | BarG | Int | 54 | 40027 | x100
PAOF | BarG | Int | 56 | 40028 | x100
TS | °C | Int | 58 | 40029 | x100
TD | °C | Int | 60 | 40030 | x100
TOH | °C | Int | 62 | 40031 | x100
MA | A | Int | 64 | 40032 | x100
CAP_% | % | Int | 66 | 40033 | x100
DOP | Bar | Int | 68 | 40034 | x100
DOF | Bar | Int | 70 | 40035 | x100
DFF | Bar | Int | 72 | 40036 | x100
Spare |  | Int | 74 | 40037 | x100
Spare |  | Int | 76 | 40038 | x100
Spare |  | Int | 78 | 40039 | x100
Spare |  | Int | 80 | 40040 | x100
DOS | Bar | Int | 82 | 40041 | x100
LCHILL | % | Int | 84 | 40042 | x100
Spare30 |  | Int | 86 | 40043 | x100
Spare31 |  | Int | 88 | 40044 | x100
Spare32 |  | Int | 90 | 40045 | x100
Others
Spare |  | Int | 92 | 40046 | x100
Spare |  | Int | 94 | 40047 | x100
Spare |  | Int | 96 | 40048 | x100
Spare |  | Int | 98 | 40049 | x100
Spare |  | Int | 100 | 40050 | x100
Spare |  | Int | 102 | 40051 | x100
Spare |  | Int | 104 | 40052 | x100
Spare |  | Int | 106 | 40053 | x100
Analog outputs
Compressor Package A (RU0001A)
Chiller MV | % | Int | 108 | 40054 | x100
Condenser VFD MV | % | Int | 110 | 40055 | x100
Compressor Package B (RU0001B)
Chiller MV | % | Int | 112 | 40056 | x100
Condenser VFD MV | % | Int | 114 | 40057 | x100
Spare | - | Int | 116 | 40058 | x100
Spare | - | Int | 118 | 40059 | x100
Spare | - | Int | 120 | 40060 | x100
Spare | - | Int | 122 | 40061 | x100
Digital Inputs
Compressor Package A (RU0001A)
Unit start PB | Unit start PB | Bool | 124 | 40062
Unit Stop PB | Unit Stop PB | Bool | 124.1 | 40062.1
Oil pump start PB | Oil pump start PB | Bool | 124.2 | 40062.2
Oil pump stop PB | Oil pump stop PB | Bool | 124.3 | 40062.3
Comp cap control remote/local switch | Comp cap control remote/local switch | Bool | 124.4 | 40062.4
lamp test PB | lamp test PB | Bool | 124.5 | 40062.5
Unit local remote select switch | Unit local remote select switch | Bool | 124.6 | 40062.6
Oil pump auto select | Oil pump auto select | Bool | 124.7 | 40062.7
Oil pump hand select | Oil pump hand select | Bool | 125 | 40062.8
Comp cap control load select | Comp cap control load select | Bool | 125.1 | 40062.9
Comp cap control unload select | Comp cap control unload select | Bool | 125.2 | 40062.A
Spare12 | Spare12 | Bool | 125.3 | 40062.B
Spare13 | Spare13 | Bool | 125.4 | 40062.C
Spare14 | Spare14 | Bool | 125.5 | 40062.D
Air cooler motor 2 vibration switch | Air cooler motor 2 vibration switch | Bool | 125.6 | 40062.E
Air cooler motor 3 vibration switch | Air cooler motor 3 vibration switch | Bool | 125.7 | 40062.F
Compressor motor running status | Compressor motor running status | Bool | 126 | 40063
Compressor fault status | Compressor fault status | Bool | 126.1 | 40063.1
Oil pump motor running status | Oil pump motor running status | Bool | 126.2 | 40063.2
Oil pump fault status | Oil pump fault status | Bool | 126.3 | 40063.3
Separator oil heater running status | Separator oil heater running status | Bool | 126.4 | 40063.4
Separator oil heater fault status | Separator oil heater fault status | Bool | 126.5 | 40063.5
Condenser motor fan 2 running status | Condenser motor fan 2 running status | Bool | 126.6 | 40063.6
Condenser motor fan 2 fault status | Condenser motor fan 2 fault status | Bool | 126.7 | 40063.7
Condenser motor fan 3 running status | Condenser motor fan 3 running status | Bool | 127 | 40063.8
Condenser motor fan 3 fault status | Condenser motor fan 3 fault status | Bool | 127.1 | 40063.9
Spare27 | Spare27 | Bool | 127.2 | 40063.A
Oil heater temp control switch | Oil heater temp control switch | Bool | 127.3 | 40063.B
Oil heater surface and box switch | Oil heater surface and box switch | Bool | 127.4 | 40063.C
Spare30 | Spare30 | Bool | 127.5 | 40063.D
Oil separator level switch | Oil separator level switch | Bool | 127.6 | 40063.E
Spare32 | Spare32 | Bool | 127.7 | 40063.F
Compressor Package B (RU0001B)
Unit start PB | Unit start PB | Bool | 128 | 40064
Unit Stop PB | Unit Stop PB | Bool | 128.1 | 40064.1
Oil pump start PB | Oil pump start PB | Bool | 128.2 | 40064.2
Oil pump stop PB | Oil pump stop PB | Bool | 128.3 | 40064.3
Comp cap control remote/local switch | Comp cap control remote/local switch | Bool | 128.4 | 40064.4
lamp test PB | lamp test PB | Bool | 128.5 | 40064.5
Unit local remote select switch | Unit local remote select switch | Bool | 128.6 | 40064.6
Oil pump auto select | Oil pump auto select | Bool | 128.7 | 40064.7
Oil pump hand select | Oil pump hand select | Bool | 129 | 40064.8
Comp cap control load select | Comp cap control load select | Bool | 129.1 | 40064.9
Comp cap control unload select | Comp cap control unload select | Bool | 129.2 | 40064.A
Spare12 | Spare12 | Bool | 129.3 | 40064.B
Spare13 | Spare13 | Bool | 129.4 | 40064.C
Spare14 | Spare14 | Bool | 129.5 | 40064.D
Air cooler motor 2 vibration switch | Air cooler motor 2 vibration switch | Bool | 129.6 | 40064.E
Air cooler motor 3 vibration switch | Air cooler motor 3 vibration switch | Bool | 129.7 | 40064.F
Compressor motor running status | Compressor motor running status | Bool | 130 | 40065
Compressor fault status | Compressor fault status | Bool | 130.1 | 40065.1
Oil pump motor running status | Oil pump motor running status | Bool | 130.2 | 40065.2
Oil pump fault status | Oil pump fault status | Bool | 130.3 | 40065.3
Separator oil heater running status | Separator oil heater running status | Bool | 130.4 | 40065.4
Separator oil heater fault status | Separator oil heater fault status | Bool | 130.5 | 40065.5
Condenser motor fan 2 running status | Condenser motor fan 2 running status | Bool | 130.6 | 40065.6
Condenser motor fan 2 fault status | Condenser motor fan 2 fault status | Bool | 130.7 | 40065.7
Condenser motor fan 3 running status | Condenser motor fan 3 running status | Bool | 131 | 40065.8
Condenser motor fan 3 fault status | Condenser motor fan 3 fault status | Bool | 131.1 | 40065.9
Spare27 | Spare27 | Bool | 131.2 | 40065.A
Oil heater temp control switch | Oil heater temp control switch | Bool | 131.3 | 40065.B
Oil heater surface and box switch | Oil heater surface and box switch | Bool | 131.4 | 40065.C
Spare30 | Spare30 | Bool | 131.5 | 40065.D
Oil separator level switch | Oil separator level switch | Bool | 131.6 | 40065.E
Spare32 | Spare32 | Bool | 131.7 | 40065.F
PLC power supply healthy | Spare32 | Bool | 132 | 40066
AUX power supply healthy |  | Bool | 132.1 | 40066.1
Barrier rack PR10 common alarm |  | Bool | 132.2 | 40066.2
Spare |  | Bool | 132.3 | 40066.3
Spare |  | Bool | 132.4 | 40066.4
Emergency stop package A |  | Bool | 132.5 | 40066.5
Emergency stop package B |  | Bool | 132.6 | 40066.6
Spare |  | Bool | 132.7 | 40066.7
Spare |  | Bool | 133 | 40066.8
Spare |  | Bool | 133.1 | 40066.9
Spare |  | Bool | 133.2 | 40066.A
Spare |  | Bool | 133.3 | 40066.B
Spare |  | Bool | 133.4 | 40066.C
Spare |  | Bool | 133.5 | 40066.D
Spare |  | Bool | 133.6 | 40066.E
Spare |  | Bool | 133.7 | 40066.F
Digital Outputs
Compressor Package A (RU0001A)
Compressor start command | Compressor start command | Bool | 134 | 40077
Compressor stop command | Compressor stop command | Bool | 134.1 | 40077.1
Oil pump start command | Oil pump start command | Bool | 134.2 | 40077.2
Oil pump stop command | Oil pump stop command | Bool | 134.3 | 40077.3
Oil heater on command | Oil heater on command | Bool | 134.4 | 40077.4
Oil heater off command | Oil heater off command | Bool | 134.5 | 40077.5
Spare | Spare23 | Bool | 134.6 | 40077.6
Spare | Spare23 | Bool | 134.7 | 40077.7
Condenser motor fan 2 start command | Condenser motor fan 2 start command | Bool | 135 | 40077.8
Condenser motor fan 2 stop command | Condenser motor fan 2 stop command | Bool | 135.1 | 40077.9
Condenser motor fan 3 start command | Condenser motor fan 3 start command | Bool | 135.2 | 40077.A
Condenser motor fan 3 stop command | Condenser motor fan 3 stop command | Bool | 135.3 | 40077.B
Spare | Spare23 | Bool | 135.4 | 40077.C
Spare | Spare23 | Bool | 135.5 | 40077.D
Spare | Spare23 | Bool | 135.6 | 40077.E
Spare | Spare23 | Bool | 135.7 | 40077.F
Comp cap control unload return SOV | Comp cap control unload return SOV | Bool | 136 | 40078
Comp cap control load supply SOV | Comp cap control load supply SOV | Bool | 136.1 | 40078.1
Comp cap control unload supply SOV | Comp cap control unload supply SOV | Bool | 136.2 | 40078.2
Comp cap control load return SOV | Comp cap control load return SOV | Bool | 136.3 | 40078.3
Hot gas SOV | Hot gas SOV | Bool | 136.4 | 40078.4
Evap oil drain SOV | Evap oil drain SOV | Bool | 136.5 | 40078.5
Spare | Spare23 | Bool | 136.6 | 40078.6
Spare | Spare23 | Bool | 136.7 | 40078.7
Unit common alarm lamp | Unit common alarm lamp | Bool | 137 | 40078.8
Unit common trip lamp | Unit common trip lamp | Bool | 137.1 | 40078.9
Unit ready to start lamp | Unit ready to start lamp | Bool | 137.2 | 40078.A
Compressor running lamp | Compressor running lamp | Bool | 137.3 | 40078.B
Oil pump running lamp | Oil pump running lamp | Bool | 137.4 | 40078.C
Spare | Spare23 | Bool | 137.5 | 40078.D
Spare | Spare23 | Bool | 137.6 | 40078.E
Spare | Spare23 | Bool | 137.7 | 40078.F
Compressor Package B (RU0001B)
Compressor start command | Compressor start command | Bool | 138 | 40079
Compressor stop command | Compressor stop command | Bool | 138.1 | 40079.1
Oil pump start command | Oil pump start command | Bool | 138.2 | 40079.2
Oil pump stop command | Oil pump stop command | Bool | 138.3 | 40079.3
Oil heater on command | Oil heater on command | Bool | 138.4 | 40079.4
Oil heater off command | Oil heater off command | Bool | 138.5 | 40079.5
Spare | Spare23 | Bool | 138.6 | 40079.6
Spare | Spare23 | Bool | 138.7 | 40079.7
Condenser motor fan 2 start command | Condenser motor fan 2 start command | Bool | 139 | 40079.8
Condenser motor fan 2 stop command | Condenser motor fan 2 stop command | Bool | 139.1 | 40079.9
Condenser motor fan 3 start command | Condenser motor fan 3 start command | Bool | 139.2 | 40079.A
Condenser motor fan 3 stop command | Condenser motor fan 3 stop command | Bool | 139.3 | 40079.B
Spare | Spare23 | Bool | 139.4 | 40079.C
Spare | Spare23 | Bool | 139.5 | 40079.D
Spare | Spare23 | Bool | 139.6 | 40079.E
Spare | Spare23 | Bool | 139.7 | 40079.F
Comp cap control unload return SOV | Comp cap control unload return SOV | Bool | 140 | 40080
Comp cap control load supply SOV | Comp cap control load supply SOV | Bool | 140.1 | 40080.1
Comp cap control unload supply SOV | Comp cap control unload supply SOV | Bool | 140.2 | 40080.2
Comp cap control load return SOV | Comp cap control load return SOV | Bool | 140.3 | 40080.3
Hot gas SOV | Hot gas SOV | Bool | 140.4 | 40080.4
Evap oil drain SOV | Evap oil drain SOV | Bool | 140.5 | 40080.5
Spare | Spare23 | Bool | 140.6 | 40080.6
Spare | Spare24 | Bool | 140.7 | 40080.7
Unit common alarm lamp | Unit common alarm lamp | Bool | 141 | 40080.8
Unit common trip lamp | Unit common trip lamp | Bool | 141.1 | 40080.9
Unit ready to start lamp | Unit ready to start lamp | Bool | 141.2 | 40080.A
Compressor running lamp | Compressor running lamp | Bool | 141.3 | 40080.B
Oil pump running lamp | Oil pump running lamp | Bool | 141.4 | 40080.C
Spare | Spare23 | Bool | 141.5 | 40080.D
Spare | Spare23 | Bool | 141.6 | 40080.E
Spare | Spare23 | Bool | 141.7 | 40080.F
Trips
Compressor Package A (RU0001A)
PS_LL | PS_LL | Bool | 142 | 40081
PS_HH | PS_HH | Bool | 142.1 | 40081.1
PD_HH | PD_HH | Bool | 142.2 | 40081.2
TD_HH | TD_HH | Bool | 142.3 | 40081.3
TOH_HH | TOH_HH | Bool | 142.4 | 40081.4
DOP_LL | DOP_LL | Bool | 142.5 | 40081.5
DOF_HH | DOF_HH | Bool | 142.6 | 40081.6
DFF_HH | DFF_HH | Bool | 142.7 | 40081.7
MA_HH | MA_HH | Bool | 143 | 40081.8
SSH_LL | SSH_LL | Bool | 143.1 | 40081.9
Comp start fail | Comp start fail | Bool | 143.2 | 40081,A
Capacity not decreasing | Capacity not decreasing | Bool | 143.3 | 40081,B
Oil level SW LL | Oil level SW LL | Bool | 143.4 | 40081,C
DOS LL | DOS LL | Bool | 143.5 | 40081,D
External trip | External trip | Bool | 143.6 | 40081.E
TS_LL | TS_LL | Bool | 143.7 | 40081.F
Spare | ALM49 | Bool | 144 | 40082
Spare | Spare23 | Bool | 144.1 | 40082.1
Spare | Spare23 | Bool | 144.2 | 40082.2
Spare | Spare23 | Bool | 144.3 | 40082.3
Spare | Spare23 | Bool | 144.4 | 40082.4
Spare | Spare23 | Bool | 144.5 | 40082.5
Spare | Spare23 | Bool | 144.6 | 40082.6
Spare | Spare23 | Bool | 144.7 | 40082.7
Spare | Spare23 | Bool | 145 | 40082.8
Spare | Spare23 | Bool | 145.1 | 40082.9
Spare | Spare23 | Bool | 145.2 | 40082,A
Spare | Spare23 | Bool | 145.3 | 40082,B
Spare | Spare23 | Bool | 145.4 | 40082,C
Spare | Spare23 | Bool | 145.5 | 40082,D
Spare | Spare23 | Bool | 145.6 | 40082,E
Spare | Spare23 | Bool | 145.7 | 40082,F
Emergency stop | MA_HH | Bool | 146 | 40083
Spare | SSH_LL | Bool | 146.1 | 40083.1
Spare | ALM49 | Bool | 146.2 | 40083.2
Spare | ALM49 | Bool | 146.3 | 40083.3
LE_HH | Oil level SW LL | Bool | 146.4 | 40083.4
LE_LL | DOS LL | Bool | 146.5 | 40083.5
Spare | ALM49 | Bool | 146.6 | 40083.6
Spare | ALM49 | Bool | 146.7 | 40083.7
Spare | ALM49 | Bool | 147 | 40083.8
Spare | Spare23 | Bool | 147.1 | 40083.9
Spare | Spare23 | Bool | 147.2 | 40083,A
Spare | Spare23 | Bool | 147.3 | 40083,B
Spare | Spare23 | Bool | 147.4 | 40083,C
Spare | Spare23 | Bool | 147.5 | 40083,D
Spare | Spare23 | Bool | 147.6 | 40083,E
Spare | Spare23 | Bool | 147.7 | 40083,F
Compressor Package B (RU0001B)
PS_LL | PS_LL | Bool | 148 | 40084
PS_HH | PS_HH | Bool | 148.1 | 40084.1
PD_HH | PD_HH | Bool | 148.2 | 40084.2
TD_HH | TD_HH | Bool | 148.3 | 40084.3
TOH_HH | TOH_HH | Bool | 148.4 | 40084.4
DOP_LL | DOP_LL | Bool | 148.5 | 40084.5
DOF_HH | DOF_HH | Bool | 148.6 | 40084.6
DFF_HH | DFF_HH | Bool | 148.7 | 40084.7
MA_HH | MA_HH | Bool | 149 | 40084.8
SSH_LL | SSH_LL | Bool | 149.1 | 40084.9
Comp start fail | Comp start fail | Bool | 149.2 | 40084,A
Capacity not decreasing | Capacity not decreasing | Bool | 149.3 | 40084,B
Oil level SW LL | Oil level SW LL | Bool | 149.4 | 40084,C
DOS LL | DOS LL | Bool | 149.5 | 40084,D
External trip | External trip | Bool | 149.6 | 40084.E
TS_LL | TS_LL | Bool | 149.7 | 40084.F
Spare | ALM49 | Bool | 150 | 40085
Spare | Spare23 | Bool | 150.1 | 40085.1
Spare | Spare23 | Bool | 150.2 | 40085.2
Spare | Spare23 | Bool | 150.3 | 40085.3
Spare | Spare23 | Bool | 150.4 | 40085.4
Spare | Spare23 | Bool | 150.5 | 40085.5
Spare | Spare23 | Bool | 150.6 | 40085.6
Spare | Spare23 | Bool | 150.7 | 40085.7
Spare | Spare23 | Bool | 151 | 40085.8
Spare | Spare23 | Bool | 151.1 | 40085.9
Spare | Spare23 | Bool | 151.2 | 40085,A
Spare | Spare23 | Bool | 151.3 | 40085,B
Spare | Spare23 | Bool | 151.4 | 40085,C
Spare | Spare23 | Bool | 151.5 | 40085,D
Spare | Spare23 | Bool | 151.6 | 40085,E
Spare | Spare23 | Bool | 151.7 | 40085,F
Emergency stop | MA_HH | Bool | 152 | 40086
Spare | SSH_LL | Bool | 152.1 | 40086.1
Spare | ALM49 | Bool | 152.2 | 40086.2
Spare | ALM49 | Bool | 152.3 | 40086.3
LE_HH | Oil level SW LL | Bool | 152.4 | 40086.4
LE_LL | DOS LL | Bool | 152.5 | 40086.5
Spare | ALM49 | Bool | 152.6 | 40086.6
Spare | ALM49 | Bool | 152.7 | 40086.7
Spare | ALM49 | Bool | 153 | 40086.8
Spare | Spare23 | Bool | 153.1 | 40086.9
Spare | Spare23 | Bool | 153.2 | 40086,A
Spare | Spare23 | Bool | 153.3 | 40086,B
Spare | Spare23 | Bool | 153.4 | 40086,C
Spare | Spare23 | Bool | 153.5 | 40086,D
Spare | Spare23 | Bool | 153.6 | 40086,E
Spare | Spare23 | Bool | 153.7 | 40086,F
Alarms
Compressor Package A (RU0001A)
PS_L | PS_L | Bool | 154 | 40087
PS_H | PS_H | Bool | 154.1 | 40087.1
PD_L | PD_L | Bool | 154.2 | 40087.2
PD_H | PD_H | Bool | 154.3 | 40087.3
TD_H | TD_H | Bool | 154.4 | 40087.4
TOH_H | TOH_H | Bool | 154.5 | 40087.5
TOH_L | TOH_L | Bool | 154.6 | 40087.6
DOP_L | DOP_L | Bool | 154.7 | 40087.7
DOP_H | DOP_H | Bool | 155 | 40087.8
DOF_H | DOF_H | Bool | 155.1 | 40087.9
DFF_H | DFF_H | Bool | 155.2 | 40087,A
MA_H | MA_H | Bool | 155.3 | 40087,B
Oil level switch L | Oil level switch L | Bool | 155.4 | 40087,C
Spare | ALM86 | Bool | 155.5 | 40087,D
Spare | ALM87 | Bool | 155.6 | 40087.E
Spare | ALM88 | Bool | 155.7 | 40087.F
Spare | ALM89 | Bool | 156 | 40088
Spare | ALM90 | Bool | 156.1 | 40088.1
Spare | ALM91 | Bool | 156.2 | 40088.2
Spare | ALM92 | Bool | 156.3 | 40088.3
Spare | ALM93 | Bool | 156.4 | 40088.4
Spare | ALM94 | Bool | 156.5 | 40088.5
Spare | ALM95 | Bool | 156.6 | 40088.6
Spare | ALM96 | Bool | 156.7 | 40088.7
Spare | ALM96 | Bool | 157 | 40088.8
Spare | ALM96 | Bool | 157.1 | 40088.9
Spare | ALM96 | Bool | 157.2 | 40088,A
Spare | ALM96 | Bool | 157.3 | 40088,B
Spare | ALM96 | Bool | 157.4 | 40088,C
Spare | ALM96 | Bool | 157.5 | 40088,D
Spare | ALM96 | Bool | 157.6 | 40088,E
Spare | ALM96 | Bool | 157.7 | 40088,F
Spare | ALM97 | Bool | 158 | 40089
LE_H | LE_H | Bool | 158.1 | 40089.1
LE_L | LE_L | Bool | 158.2 | 40089.2
Separator oil heater operation failure | Separator oil heater operation failure | Bool | 158.3 | 40089.3
Condenser fan M-02 operation failure | Condenser fan M-02 operation failure | Bool | 158.4 | 40089.4
Condenser fan M-03 operation failure | Condenser fan M-03 operation failure | Bool | 158.5 | 40089.5
Oil pump motor fault | Oil pump motor fault | Bool | 158.6 | 40089.6
Separator oil heater fault | Separator oil heater fault | Bool | 158.7 | 40089.7
Condenser M-02 fault | Condenser M-02 fault | Bool | 159 | 40089.8
Condenser M-03 fault | Condenser M-03 fault | Bool | 159.1 | 40089.9
Separator oil heater trip | Separator oil heater trip | Bool | 159.2 | 40089,A
Condenser M-03 trip | Condenser M-03 trip | Bool | 159.3 | 40089,B
Condenser M-02 trip | Condenser M-02 trip | Bool | 159.4 | 40089,C
Spare | ALM97 | Bool | 159.5 | 40089,D
Spare | ALM97 | Bool | 159.6 | 40089,E
Spare | ALM97 | Bool | 159.7 | 40089,F
Compressor Package B (RU0001B)
PS_L | PS_L | Bool | 160 | 40090
PS_H | PS_H | Bool | 160.1 | 40090.1
PD_L | PD_L | Bool | 160.2 | 40090.2
PD_H | PD_H | Bool | 160.3 | 40090.3
TD_H | TD_H | Bool | 160.4 | 40090.4
TOH_H | TOH_H | Bool | 160.5 | 40090.5
TOH_L | TOH_L | Bool | 160.6 | 40090.6
DOP_L | DOP_L | Bool | 160.7 | 40090.7
DOP_H | DOP_H | Bool | 161 | 40090.8
DOF_H | DOF_H | Bool | 161.1 | 40090.9
DFF_H | DFF_H | Bool | 161.2 | 40090,A
MA_H | MA_H | Bool | 161.3 | 40090,B
Oil level switch L | Oil level switch L | Bool | 161.4 | 40090,C
Spare | ALM86 | Bool | 161.5 | 40090,D
Spare | ALM87 | Bool | 161.6 | 40090,E
Spare | ALM88 | Bool | 161.7 | 40090,F
Spare | ALM89 | Bool | 162 | 40091
Spare | ALM90 | Bool | 162.1 | 40091.1
Spare | ALM91 | Bool | 162.2 | 40091.2
Spare | ALM92 | Bool | 162.3 | 40091.3
Spare | ALM93 | Bool | 162.4 | 40091.4
Spare | ALM94 | Bool | 162.5 | 40091.5
Spare | ALM95 | Bool | 162.6 | 40091.6
Spare | ALM96 | Bool | 162.7 | 40091.7
Spare | ALM97 | Bool | 163 | 40091.8
Spare | ALM97 | Bool | 163.1 | 40091.9
Spare | ALM97 | Bool | 163.2 | 40091,A
Spare | ALM97 | Bool | 163.3 | 40091,B
Spare | ALM97 | Bool | 163.4 | 40091,C
Spare | ALM97 | Bool | 163.5 | 40091,D
Spare | ALM97 | Bool | 163.6 | 40091,E
Spare | ALM97 | Bool | 163.7 | 40091,F
Spare | ALM97 | Bool | 164 | 40092
LE_H | LE_H | Bool | 164.1 | 40092.1
LE_L | LE_L | Bool | 164.2 | 40092.2
Separator oil heater operation failure | Separator oil heater operation failure | Bool | 164.3 | 40092.3
Condenser fan M-02 operation failure | Condenser fan M-02 operation failure | Bool | 164.4 | 40092.4
Condenser fan M-03 operation failure | Condenser fan M-03 operation failure | Bool | 164.5 | 40092.5
Oil pump motor fault | Oil pump motor fault | Bool | 164.6 | 40092.6
Separator oil heater fault | Separator oil heater fault | Bool | 164.7 | 40092.7
Condenser M-02 fault | Condenser M-02 fault | Bool | 165 | 40092.8
Condenser M-03 fault | Condenser M-03 fault | Bool | 165.1 | 40092.9
Separator oil heater trip | Separator oil heater trip | Bool | 165.2 | 40092,A
Condenser M-03 trip | Condenser M-03 trip | Bool | 165.3 | 40092,B
Condenser M-02 trip | Condenser M-02 trip | Bool | 165.4 | 40092,C
Spare | ALM97 | Bool | 165.5 | 40092,D
Spare | ALM97 | Bool | 165.6 | 40092,E
Spare | ALM97 | Bool | 165.7 | 40092,F
END BYTE |  |  | 165.3