## Type3
Rev.
1 | Item | 3
2 | DUTY | Level Switches
3 | INSTALLATION LOCATION | OUTDOOR
4 | INSTALLATION METHOD | -
5 | AMBIENT TEMP MIN / MAX | -20 °C / 48 °C
6 | CABLE TECHNICAL DATA
7 | MAKE | LATER
8 | TYPE | As per EN50288-7
9 | CONDUCTORS | Stranded Copper - IEC 60228 class 2
10 | INSULATION | XLPE
11 | CORE / PAIR / TRIAD | Twisted Pair
12 | IDENTIFICATION | Black - white
13 | SCREENING | Collective Aluminium/Maylar tape + tinned copper drain wire
14 | BEDDING | PVC
15 | ARMOUR | Galvanised Steel Wire Armour (SWA)
16 | OUTER JACKET | PVC
17 | OUTER SHEATH COLOUR | Gray
18 | CROSS SECTION | 1.5 mm2
19 | NUMBER OF CORES / PARE / TRIADS | 2 Pair
20 | MAX. OPERATING VOLTAGE | 300 / 500 Volt
21 | MIN. OPERATING TEMPERATURE | -20 °C
22 | MAX. OPERATING TEMPERATURE | +60 °C
23 | CONDUCTOR MAXIMUM TEMPERATURE | +90 °C
24
25 | INNER SHEATH DIAMETER | Later
26 | OUTER SHEATH DIAMETER | Later
27
28 | FLAME RETARDANT | IEC60332-1-2 / IEC 60332-3-24 (cat.C)
29
30
31
32
33
34
35