## Cover
|  | Toase-ehe Park Sanati Gohar Ofogh Petrochemical Co. CONCEPTUAL, BASIC and DETAIL DESIGN ENGINEERING OF STYRENE PARK OFFSITE |  | Purchaser Logo
Document Title: Inspection and Test Plan (ITP)
|  | Document No.: E1027-FPA-VD-QC-ITP-001 |  | Rev.: R0 | Page 1 of 7
STYRENE PARK OFFSITE Document Title: Inspection and Test Plan
R0 | 5-Aug-2024 | IFA | F. Baviye | N. Abnavi | N. Abnavi
Rev. | Issued Date | DESCRIPTION | PREPARED | CHECKED | APPROVED

## Index
|  |  |  | Toase-ehe Park Sanati Gohar Ofogh Petrochemical Co. CONCEPTUAL, BASIC and DETAIL DESIGN ENGINEERING OF STYRENE PARK OFFSITE | [8 empty] | Purchaser Logo
Document Title: Inspection and Test Plan (ITP)
|  |  |  | Document No.: E1027-FPA-VD-QC-ITP-001 | [8 empty] | Rev.: R0 | Page 2 of 7
Page | Revisions | [6 empty] | Page | Revisions
| R0 | R1 | R2 | R3 | R4 | R5 | R6 |  | R0 | R1 | R2 | R3 | R4 | R5 | R6
1 | X | [6 empty] | 41
2 | X | [6 empty] | 42
3 | X | [6 empty] | 43
4 | X | [6 empty] | 44
5 | X | [6 empty] | 45
6 | X | [6 empty] | 46
7 | X | [6 empty] | 47
8 | [7 empty] | 48
9 | [7 empty] | 49
10 | [7 empty] | 50
11 | [7 empty] | 51
12 | [7 empty] | 52
13 | [7 empty] | 53
14 | [7 empty] | 54
15 | [7 empty] | 55
16 | [7 empty] | 56
17 | [7 empty] | 57
18 | [7 empty] | 58
19 | [7 empty] | 59
20 | [7 empty] | 60
21 | [7 empty] | 61
22 | [7 empty] | 62
23 | [7 empty] | 63
24 | [7 empty] | 64
25 | [7 empty] | 65
26 | [7 empty] | 66
27 | [7 empty] | 67
28 | [7 empty] | 68
29 | [7 empty] | 69
30 | [7 empty] | 70
31 | [7 empty] | 71
32 | [7 empty] | 72
33 | [7 empty] | 73
34 | [7 empty] | 74
35 | [7 empty] | 75
36 | [7 empty] | 76
37 | [7 empty] | 77
38 | [7 empty] | 78
39 | [7 empty] | 79
40 | [7 empty] | 80

## 1
|  | Inspection & Test Plan (ITP) | [5 empty] | DOC. NO.: E1027-FPA-VD-QC-ITP-001
OWNER: Toase-ehe Park Sanati Gohar Ofogh Petrochemical Co. |  |  | PROJECT: STYRENE PARK OFFSITE |  |  |  |  | PAGE: 3 of 7 | REV.: 00
PROJECT NO.: HX-127 |  |  | ITEM NO.: |  |  | ITEM DESCRIPTION: CHILLER (EVAPORATOR)
ITEM NO. | QUALITY VERIFICATION ACTIVITY |  |  | REFERENCE PROCEDURE/ DOCUMENT | ACCEPTANCE CRITERIA | VERIFYING DOCUMENTS | INSPECTION POINT
[7 empty] | VENDOR | HSE | OWNER/TPI
NOTE:
1. Description of Inspection Points
HOLD POINT (HP) |  | The designated feature shall to be witnessed by OWNER INSPECTOR. Vendor/manufacturer is to notify project quality coordinator two weeks prior to performing the designated feature. Activities do not proceed until the continuation of work is permitted by project quality coordinator or waived in writing by him (“inspection waiver”).
WITNESS POINT (WP) |  | The designated feature is to be witnessed by OWNER INSPECTOR. Vendor/manufacturer is to notify project quality coordinator two weeks prior to performing the designated feature. If the INSPECTOR fails to be present, activities may proceed without witnessing or waiving of the inspection as will be decided by Project quality coordinator.
RANDOM INSPECTION (RI) |  | The inspection of the designated feature will take place during inspection visits as a standard performance. Vendor/manufacturer does not have to notify Project quality coordinator prior to performing the designated feature. Activities may proceed without witnessing or waiving by Project quality coordinator
REVIEW DOCUMENTATION (RD/RA) |  | Documentation will be reviewed/approved by Project Engineering team or INSPECTOR depend the nature of documents (refer to VDIS in order to find that documents which shall be reviewed & approved by project engineering team and/or inspector).
2. Definition
Vendor: |  | Farnikan Pars Avin
Owner: |  | Toase-ehe Park Sanati Gohar Ofogh Petrochemical Co.
Consultant. |  | Hamian Sanat Energy
TPI: |  | Third Party Inspector
| LEGEND: | HOLD POINT(HP) |  | WITNESS POINT(WP) | RANDOM INSPECTION(RI) |  | REVIEW DOCUMENTATION(RD/RA)
-

## 2
|  | Inspection & Test Plan (ITP) | [5 empty] | DOC. NO.: E1027-FPA-VD-QC-ITP-001
OWNER: Toase-ehe Park Sanati Gohar Ofogh Petrochemical Co. |  |  | PROJECT: STYRENE PARK OFFSITE |  |  |  |  | PAGE: 4 of 7 | REV.: 00
PROJECT NO.: HX-127 |  |  | ITEM NO.: |  |  | ITEM DESCRIPTION: CHILLER (EVAPORATOR)
ITEM NO. | QUALITY VERIFICATION ACTIVITY |  |  | REFERENCE PROCEDURE/ DOCUMENT | ACCEPTANCE CRITERIA | VERIFYING DOCUMENTS | INSPECTION POINT
[7 empty] | VENDOR | HSE | OWNER/TPI
1 | Before Fabrication
1-1 | Review & Approval of Documents | - Mechanical Calculation (If Any) |  |  |  | Vendor Document Index & Schedule (APP. VDIS) | HP | RA | RA
- Drawings (If Any)
- Inspection & Test Plan
|  | - Welding Document |  | Vendor Document Index & Schedule
|  | (WPS,PQR,Welding Map & NDT Map) |  | ASME Sec. V
|  | - WPQ & NDE Operator Certificates |  | ASME Sec. VIII. Div.1
|  | -QC Procedure: NDT Procedure,… |  | ASME Sec. IX
|  | - PWHT Procedure (if Any) |  | Project Specification
-Hydrostatic Test Procedure
-Painting Procedure
1-2 | Pre-Inspection Meeting (PIM) | Pre-Inspection Meeting (PIM) |  | Pre-Inspection Meeting Agenda |  | Minutes of Meeting | HP | HP | HP
2 | Material Inspection
2-1 | Final Inspection of Material Receiving for Pressure Retaining Parts (Plate, Flange, Pipe,…) & Component (Tube, Tubesheet, Baffle,…) | - Check of Material Test Certificate(MTC) |  | ASME Sec. II | ASME Sec. II Part A | Check Advice | HP | WP | WP
a. Confirmation of Heat No.
|  | c. Mechanical properties |  | MTC/Lab. Result (if any) | Certificate Type : EN10204 Type 3.1
|  | d. Other tests |  | Fabrication Drawings
|  | (NDE, Simulation Impact, etc.- if any) |  | TEMA
- Visual & Dimensional Check of Materials
2-2 | Welding Consumable Control | - Visual Inspection |  | WPS & PQR | WPS & PQR | - | HP | RI | RI
|  |  |  | ASME Sec. II, Part C | ASME Sec. II, Part C
3 | Fabrication and Inspection of Shellside
3-1 | Transfer of Material Identification Before Cutting | -Visual Inspection |  | ASME Sec. II Fabrication Drawings |  | - | HP | RI | RI
3-2 | Marking, Cutting, Rolling & Driling of Plate (If Any) | -Visual & Dimensional Inspection |  | Fabrication Drawings |  | - | HP | RI | RI
| LEGEND: | HOLD POINT(HP) |  | WITNESS POINT(WP) | RANDOM INSPECTION(RI) |  | REVIEW DOCUMENTATION(RD/RA)

## 3
|  | Inspection & Test Plan (ITP) | [5 empty] | DOC. NO.: E1027-FPA-VD-QC-ITP-001
OWNER: Toase-ehe Park Sanati Gohar Ofogh Petrochemical Co. |  |  | PROJECT: STYRENE PARK OFFSITE |  |  |  |  | PAGE: 5 of 7 | REV.: 00
PROJECT NO.: HX-127 |  |  | ITEM NO.: |  |  | ITEM DESCRIPTION: CHILLER (EVAPORATOR)
ITEM NO. | QUALITY VERIFICATION ACTIVITY |  |  | REFERENCE PROCEDURE/ DOCUMENT | ACCEPTANCE CRITERIA | VERIFYING DOCUMENTS | INSPECTION POINT
[7 empty] | VENDOR | HSE | OWNER/TPI
3 | Fabrication and Inspection of Shellside
3-3 | Edge Preparation & Fit up Alignment Check (For Long. & Circum. Joints, Nozzle Neck to Flange Joints) | -Visual & Dimensional Inspection |  | Fabrication Drawings |  | Report | HP | RI | RI
|  | - 100% PT on Weld Bevel (for Thk>=30mm) |  | NDT Procedure
Welding Book (WPS, PQR, Welding&NDT Map)
3-4 | Welding Inspection (Welding of Long. & Circum. Joints, Nozzle Neck to Flange Joints) | - 100% Visual Inspection |  | Welding Book (WPS, PQR, Welding&NDT Map) |  | Report | HP | RI | RI
-100% MT or PT on Back Grinding (if any)
|  | -NDT per App.NDT Map |  | NDT Procedure
3-5 | Marking & Cutting of Nozzle Opening | - Check of nozzle marking |  | Fabrication Drawings |  | Report | HP | RI | RI
-Dimensional Inspection of Opening
( Elevation/Orientation/ Opening Size)
3-6 | Edge Preparation & Fit up Alignment Check (For Nozzle to shell joints) | -Visual & Dimensional Inspection |  | Fabrication Drawings |  | Report | HP | RI | RI
|  | - 100% PT on Weld Bevel (for Thk>=30mm) |  | Welding Book (WPS, PQR, Welding&NDT Map)
3-7 | Welding Inspection (Welding of Nozzle to shell joints) | - 100% Visual Inspection |  | Welding Book (WPS, PQR, Welding&NDT Map) |  | Report | HP | RI | RI
|  | -100% MT or PT on Back Grinding (if any) |  | NDT Procedure
- UT of Nozzle to Shell Welds
3-8 | Edge Preparation & Fit up Alignment and Welding Check of Saddle and Attachments | -Visual & Dimensional Inspection |  | Fabrication Drawings |  | Report | HP | RI | RI
|  | - 10% PT |  | Welding Book (WPS, PQR, Welding&NDT Map)
3-9 | Final Visual & Dimensional Inspection | -Dimensional inspection: Overall length |  | Fabrication Drawing |  | Report | HP | RI | RI
|  | ID Check,Location of nozzle,… |  | ASME Sec. VIII, Div.1, UW-35
|  | Visual for completed surface of internal &external welds,… |  | TEMA Fig. F-1~F-3, Purchase Order
All Vendor Procedure and QC verified test / Inspection reports / records
4 | Fabrication and Inspection of Channel
4-1 | Transfer of Material Identification Before Cutting | -Visual Inspection |  | ASME Sec. II Fabrication Drawings |  | - | HP | RI | RI
4-2 | Marking, Cutting, Rolling & Driling of Plate (If Any) | -Visual & Dimensional Inspection |  | Fabrication Drawings |  | - | HP | RI | RI
| LEGEND: | HOLD POINT(HP) |  | WITNESS POINT(WP) | RANDOM INSPECTION(RI) |  | REVIEW DOCUMENTATION(RD/RA)

## 4
|  | Inspection & Test Plan (ITP) | [5 empty] | DOC. NO.: E1027-FPA-VD-QC-ITP-001
OWNER: Toase-ehe Park Sanati Gohar Ofogh Petrochemical Co. |  |  | PROJECT: STYRENE PARK OFFSITE |  |  |  |  | PAGE: 6 of 7 | REV.: 00
PROJECT NO.: HX-127 |  |  | ITEM NO.: |  |  | ITEM DESCRIPTION: CHILLER (EVAPORATOR)
ITEM NO. | QUALITY VERIFICATION ACTIVITY |  |  | REFERENCE PROCEDURE/ DOCUMENT | ACCEPTANCE CRITERIA | VERIFYING DOCUMENTS | INSPECTION POINT
[7 empty] | VENDOR | HSE | OWNER/TPI
4 | Fabrication and Inspection of Channel
4-3 | Edge Preparation & Fit up Alignment Check (For Long. & Circum. Joints, Nozzle Neck to Flange Joints) | -Visual & Dimensional Inspection |  | Fabrication Drawings |  | Report | HP | RI | RI
|  | - 100% PT on Weld Bevel (for Thk>=30mm) |  | Welding Book (WPS, PQR, Welding&NDT Map)
4-4 | Welding Inspection (Welding of Long. & Circum. Joints, Nozzle Neck to Flange Joints) | - 100% Visual Inspection |  | Welding Book (WPS, PQR, Welding&NDT Map) |  | Report | HP | RI | RI
-100% MT or PT on Back Grinding (if any)
|  | -NDT per NDT Map |  | NDT Procedure
4-5 | Marking & Cutting of Nozzle Opening | - Check of nozzle marking |  | Fabrication Drawings |  | - | HP | RI | RI
-Dimensional Inspection of Opening
( Elevation/Orientation/ Opening Size)
4-6 | Edge Preparation & Fit up Alignment Check (For Nozzle to Channel Joints) | -Visual & Dimensional Inspection |  | Fabrication Drawings |  | Report | HP | RI | RI
|  | - 100% PT on Weld Bevel (for Thk>=30mm) |  | Welding Book (WPS, PQR, Welding&NDT Map)
4-7 | Welding Inspection (Welding of Nozzle(For Nozzle to Channel Joints) | - 100% Visual Inspection |  | NDT Procedure |  | Report | HP | RI | RI
-100% PT or MT on Back Grinding (if any)
|  | - UT of Nozzle to Channel Welds |  | Welding Book (WPS, PQR, Welding Map)
4-8 | Final Visual & Dimensional Inspection | -Dimensional inspection: Overall length |  | Fabrication Drawings |  | Report | HP | RI | RI
|  | ID Check,Location of nozzle,… |  | ASME Sec. VIII, Div1, UW-35
|  | Visual for completed surface of internal &external welds,… |  | TEMA Fig. F-1~F-3, Purchase Order
All Vendor Procedure and QC verified test / Inspection reports / records
5 | Fabrication and Inspection of Bundle
5-1 | Tube bundle Assembly (Baffle Arrangement/Using Spacer&Tie Rods, Tubes Insertion …) | - Visual & dimensional Check |  | Fabrication Drawings |  | - | HP | RI | RI
5-2 | Cleaning of Tube Ends and Tubesheet Weld Area | - Visual Inspection |  | - |  | - | HP | - | -
| LEGEND: | HOLD POINT(HP) |  | WITNESS POINT(WP) | RANDOM INSPECTION(RI) |  | REVIEW DOCUMENTATION(RD/RA)

## 5
|  | Inspection & Test Plan (ITP) | [5 empty] | DOC. NO.: E1027-FPA-VD-QC-ITP-001
OWNER: Toase-ehe Park Sanati Gohar Ofogh Petrochemical Co. |  |  | PROJECT: STYRENE PARK OFFSITE |  |  |  |  | PAGE: 7 of 7 | REV.: 00
PROJECT NO.: HX-127 |  |  | ITEM NO.: |  |  | ITEM DESCRIPTION: CHILLER (EVAPORATOR)
ITEM NO. | QUALITY VERIFICATION ACTIVITY |  |  | REFERENCE PROCEDURE/ DOCUMENT | ACCEPTANCE CRITERIA | VERIFYING DOCUMENTS | INSPECTION POINT
[7 empty] | VENDOR | HSE | OWNER/TPI
5 | Fabrication and Inspection of Bundle
5-3 | Welding Inspection of Tube to Tubesheet Joints | - Visual and Dimensional Control |  | Fabrication Drawings |  | Report | HP | RI | RI
Welding Book (WPS, PQR, Welding&NDT Map)
5-4 | Insertion Tubebundle in Shell | - Visual Control |  | - |  | - | HP | - | -
5-5 | Air-Soap Test | Pressure 0.5 bar on Shell side |  | - |  | Report | HP | RI | RI
5-6 | Tube Expanding Inspection | - Check of Expanding Ratio |  | Fabrication Drawing |  | Report | HP | RI | RI
- Expanded Length
|  | 1% or 20 hole shall be reported |  | Tube Expanding Procedure
5-7 | NDE after Expansion | - 100% PT |  | Welding Book (WPS, PQR, Welding Map&NDT map) |  | Report | HP | RI | RI
NDT Procedure
6 | Final Inspection
6-1 | Final Visual & Dimensional Inspection |  |  | AS-Built Drawing |  | Report | HP | WP | WP
6-2 | Pressure Test (Hydrostatic Test) - 1st Shell Side - 2nd Tube Side |  |  | Fabrication Drawings, ASME Sec. VIII, Div.1, Hydro. Test Procedure |  | Report | HP | WP | WP
6-3 | Blasting & Painting Inspection |  |  | Project Spec. & Painting Procedure |  | Report | HP | RI | RI
6-4 | Marking / Packing & Shipping | -Name Plate Check |  | Spare Part List |  | Packing List | HP | WP | WP
-Spare Parts Check (if any)
|  | - Bolting and gaskets for blind flanges |  | AS-Built Drawing
|  | - N2 Purging(if any), … |  | N2 Purging Procedure
6-5 | Release for Shipment |  |  | - |  | Release Note | HP | HP | HP
6-6 | Manufacturer's Data Book |  |  | Manufacturer's Data Book Index |  | MDB | HP | RA | RA
| LEGEND: | HOLD POINT(HP) |  | WITNESS POINT(WP) | RANDOM INSPECTION(RI) |  | REVIEW DOCUMENTATION(RD/RA)