STYRENE PARK OFFSITE Document Title: Electrical Motor Data Sheet

| R3 | 06-11-2024 | IFA | F.Aghaienezhad | J.Beigloo | A.Gholizadeh |
| --- | --- | --- | --- | --- | --- |
| R2 | 06-10-2024 | IFA | F.Aghaienezhad | J.Beigloo | A.Gholizadeh |
| R1 | 11-08-2024 | IFA | F.Aghaienezhad | J.Beigloo | A.Gholizadeh |
| R0 | 22-06-2024 | IFA | F.Aghaienezhad | J.Beigloo | A.Gholizadeh |
| Rev. | Issued Date | DESCRIPTION | PREPARED | CHECKED | APPROVED |

REVISION RECORD SHEET

| Page Page | Revisions |  |  |  |  |  |  |  | Page | Revisions |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | R0 | R1 | R2 | R3 | R4 | R5 | R6 |  |  | R0 | R1 | R2 | R3 | R4 | R5 | R6 |
| 1 | X | X | X | X |  |  |  |  | 41 |  |  |  |  |  |  |  |
| 2 | X | X | X | X |  |  |  |  | 42 |  |  |  |  |  |  |  |
| 3 | X | X | X | X |  |  |  |  | 43 |  |  |  |  |  |  |  |
| 4 |  | X | X |  |  |  |  |  | 44 |  |  |  |  |  |  |  |
| 5 |  | X | X |  |  |  |  |  | 45 |  |  |  |  |  |  |  |
| 6 |  | X | X |  |  |  |  |  | 46 |  |  |  |  |  |  |  |
| 7 |  | X | X |  |  |  |  |  | 47 |  |  |  |  |  |  |  |
| 8 |  | X | X |  |  |  |  |  | 48 |  |  |  |  |  |  |  |
| 9 |  | X | X |  |  |  |  |  | 49 |  |  |  |  |  |  |  |
| 10 |  | X | X |  |  |  |  |  | 50 |  |  |  |  |  |  |  |
| 11 |  | X |  |  |  |  |  |  | 51 |  |  |  |  |  |  |  |
| 12 |  | X |  |  |  |  |  |  | 52 |  |  |  |  |  |  |  |
| 13 |  | X |  |  |  |  |  |  | 53 |  |  |  |  |  |  |  |
| 14 |  | X |  |  |  |  |  |  | 54 |  |  |  |  |  |  |  |
| 15 |  |  |  |  |  |  |  |  | 55 |  |  |  |  |  |  |  |
| 16 |  |  |  |  |  |  |  |  | 56 |  |  |  |  |  |  |  |
| 17 |  |  |  |  |  |  |  |  | 57 |  |  |  |  |  |  |  |
| 18 |  |  |  |  |  |  |  |  | 58 |  |  |  |  |  |  |  |
| 19 |  |  |  |  |  |  |  |  | 59 |  |  |  |  |  |  |  |
| 20 |  |  |  |  |  |  |  |  | 60 |  |  |  |  |  |  |  |
| 21 |  |  |  |  |  |  |  |  | 61 |  |  |  |  |  |  |  |
| 22 |  |  |  |  |  |  |  |  | 62 |  |  |  |  |  |  |  |
| 23 |  |  |  |  |  |  |  |  | 63 |  |  |  |  |  |  |  |
| 24 |  |  |  |  |  |  |  |  | 64 |  |  |  |  |  |  |  |
| 25 |  |  |  |  |  |  |  |  | 65 |  |  |  |  |  |  |  |
| 26 |  |  |  |  |  |  |  |  | 66 |  |  |  |  |  |  |  |
| 27 |  |  |  |  |  |  |  |  | 67 |  |  |  |  |  |  |  |
| 28 |  |  |  |  |  |  |  |  | 68 |  |  |  |  |  |  |  |
| 29 |  |  |  |  |  |  |  |  | 69 |  |  |  |  |  |  |  |
| 30 |  |  |  |  |  |  |  |  | 70 |  |  |  |  |  |  |  |
| 31 |  |  |  |  |  |  |  |  | 71 |  |  |  |  |  |  |  |
| 32 |  |  |  |  |  |  |  |  | 72 |  |  |  |  |  |  |  |
| 33 |  |  |  |  |  |  |  |  | 73 |  |  |  |  |  |  |  |
| 34 |  |  |  |  |  |  |  |  | 74 |  |  |  |  |  |  |  |
| 35 |  |  |  |  |  |  |  |  | 75 |  |  |  |  |  |  |  |
| 36 |  |  |  |  |  |  |  |  | 76 |  |  |  |  |  |  |  |
| 37 |  |  |  |  |  |  |  |  | 77 |  |  |  |  |  |  |  |
| 38 |  |  |  |  |  |  |  |  | 78 |  |  |  |  |  |  |  |
| 39 |  |  |  |  |  |  |  |  | 79 |  |  |  |  |  |  |  |
| 40 |  |  |  |  |  |  |  |  | 80 |  |  |  |  |  |  |  |

| MOTOR BASIC DATA (1158) |  |
| --- | --- |
| INSTALLATION SITE |  |
| QUANTITY/ Tag number | 4/ RU0001A-M-02, RU0001A-M-03, RU0001B-M-02, RU0001B-M-02 |
| BRAND-MODEL | Marathon- E3ABL |
| RATED POWER | 7.5 kw |
| SUPPLY VOLTS | 400±5% |
| FREQUENCY | 50±2% |
| NUMBER OF POLE | 4 |
| WINDING CONNECTIONS/ROTATION | Delta |
| COUPLING TYPE | V-Belt(Belt & Pulley) |
| NOMIAL SPEED | 1500 rpm |
| DUTY CATEGORY | S1 |
| INVERTER DUTY | YES |
| ALTITUDE | 20 m |
| AMBIENT TEMPRATURE MIN/MAX | 5/48 C |
| RELATIVE HUMIDITY (RH) | 65% |
| STARTING METHOD | 2-DOL /2-VFD |
| CABLE GLAND SUPLIED | YES |
| DIRECTION OR ROTATION | Both |
| ISULATION CLASS/TEMP. RISE | F/B |
| COOLING | (IC 411) |
| AREA CLASSIFICATION | Ex db IIB T4 |
| WINDING TEMPERATURE . DETECTORS (PTC RELAY) | N.A |
| ANTI-CONDANATION HEATER (SPACE HEATER) | N.A |
| MOUNTING (TYPE OF INSTALATION) | IMV3 |
| PROTECTION DEGREE FOR MOTOR/FOR TERMINAL BOX | IP55//IP55 |
| ROTOR CAGE MATERIAL (AL) | CAST IRON |
| PAINT SYSTEM | STANDARD COLOR-RAL (5015) |
| CABLE TYPE AND SIZE (FEEDER CABLE BY CLIENT) MAIN HEATER PTC | 18~21 mm |
|  | N.A |
|  | N.A |
| THERED (GLAND) ENTRY MAIN HEATER PTC | 2XM32 |
|  | N.A |
|  | N.A |
| EARTH TERMINALS | IN & EXT |
| MAX NOISE LEVEL (AT ONE METER) | < 85 |
| LIFTING DEVICE | YES |
| DRAIN PLUGS | NO |
| NO OF PHASE | 3 |
| IE (EFFICIENCY CLASS) | IE=3 |
| PF (COS &) | 0.84 |
| TYPE TEST | NO |
| MOTOR SUITABLE FOR VCDS (Y/N) | NO |
| CURVE & OUTLINE & COMPLETE CATALOUGE (Y/N) | YES |