STYRENE PARK OFFSITE Document Title Inspection And Test (ITP) FOR Refrigeration Unit-Package (RU)

| R3 | 31-08-2024 | IFA | F.SH | M.O | A.M |
| --- | --- | --- | --- | --- | --- |
| R2 | 07-04-2024 | IFA | F.SH | M.O | A.M |
| R1 | 18-09-2023 | IFA | N.B | F.SH | A.M |
| R0 | 17-09-2023 | IFA | N.B | F.SH | A.M |
| Rev. | Issued Date | DESCRIPTION | PREPARED | CHECKED | APPROVED |

REVISION RECORD SHEET

| Page Page | Revisions |  |  |  |  |  |  |  | Page | Revisions |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | R0 | R1 | R2 | R3 | R4 | R5 | R6 |  |  | R0 | R1 | R2 | R3 | R4 | R5 | R6 |
| 1 | × | × | × | × |  |  |  |  | 41 |  |  |  |  |  |  |  |
| 2 | × | × | × | × |  |  |  |  | 42 |  |  |  |  |  |  |  |
| 3 | × | × | × | × |  |  |  |  | 43 |  |  |  |  |  |  |  |
| 4 | × | × | × | × |  |  |  |  | 44 |  |  |  |  |  |  |  |
| 5 | × | × | × | × |  |  |  |  | 45 |  |  |  |  |  |  |  |
| 6 | × | × | × | × |  |  |  |  | 46 |  |  |  |  |  |  |  |
| 7 | × | × | × | × |  |  |  |  | 47 |  |  |  |  |  |  |  |
| 8 | × | × | × | × |  |  |  |  | 48 |  |  |  |  |  |  |  |
| 9 |  |  |  | × |  |  |  |  | 49 |  |  |  |  |  |  |  |
| 10 |  |  |  | × |  |  |  |  | 50 |  |  |  |  |  |  |  |
| 11 |  |  |  | × |  |  |  |  | 51 |  |  |  |  |  |  |  |
| 12 |  |  |  | × |  |  |  |  | 52 |  |  |  |  |  |  |  |
| 13 |  |  |  |  |  |  |  |  | 53 |  |  |  |  |  |  |  |
| 14 |  |  |  |  |  |  |  |  | 54 |  |  |  |  |  |  |  |
| 15 |  |  |  |  |  |  |  |  | 55 |  |  |  |  |  |  |  |
| 16 |  |  |  |  |  |  |  |  | 56 |  |  |  |  |  |  |  |
| 17 |  |  |  |  |  |  |  |  | 57 |  |  |  |  |  |  |  |
| 18 |  |  |  |  |  |  |  |  | 58 |  |  |  |  |  |  |  |
| 19 |  |  |  |  |  |  |  |  | 59 |  |  |  |  |  |  |  |
| 20 |  |  |  |  |  |  |  |  | 60 |  |  |  |  |  |  |  |
| 21 |  |  |  |  |  |  |  |  | 61 |  |  |  |  |  |  |  |
| 22 |  |  |  |  |  |  |  |  | 62 |  |  |  |  |  |  |  |
| 23 |  |  |  |  |  |  |  |  | 63 |  |  |  |  |  |  |  |
| 24 |  |  |  |  |  |  |  |  | 64 |  |  |  |  |  |  |  |
| 25 |  |  |  |  |  |  |  |  | 65 |  |  |  |  |  |  |  |
| 26 |  |  |  |  |  |  |  |  | 66 |  |  |  |  |  |  |  |
| 27 |  |  |  |  |  |  |  |  | 67 |  |  |  |  |  |  |  |
| 28 |  |  |  |  |  |  |  |  | 68 |  |  |  |  |  |  |  |
| 29 |  |  |  |  |  |  |  |  | 69 |  |  |  |  |  |  |  |
| 30 |  |  |  |  |  |  |  |  | 70 |  |  |  |  |  |  |  |
| 31 |  |  |  |  |  |  |  |  | 71 |  |  |  |  |  |  |  |
| 32 |  |  |  |  |  |  |  |  | 72 |  |  |  |  |  |  |  |
| 33 |  |  |  |  |  |  |  |  | 73 |  |  |  |  |  |  |  |
| 34 |  |  |  |  |  |  |  |  | 74 |  |  |  |  |  |  |  |
| 35 |  |  |  |  |  |  |  |  | 75 |  |  |  |  |  |  |  |
| 36 |  |  |  |  |  |  |  |  | 76 |  |  |  |  |  |  |  |
| 37 |  |  |  |  |  |  |  |  | 77 |  |  |  |  |  |  |  |
| 38 |  |  |  |  |  |  |  |  | 78 |  |  |  |  |  |  |  |
| 39 |  |  |  |  |  |  |  |  | 79 |  |  |  |  |  |  |  |
| 40 |  |  |  |  |  |  |  |  | 80 |  |  |  |  |  |  |  |

Table of Contents

1- General .............................................................................................................    4

1.1 Introduction.............................................................................................................    4

1.2 Definitions ..............................................................................................................    4

2- Abbreviations.....................................................................................................    4

- General

  - Introduction

This document covers Inspection & Test Plan for Refrigeration unit package (RU).

  - Definitions

The following terms and abbreviations are used in the present document

| Item | Correspondences |
| --- | --- |
| Project | STYRENE PARK OFFSITE |
| Client | Pad Jam Polymer Development Company |
| Purchaser | Petro electric Energy Development Company |
| Consultant | Gohar Ofogh |
| Vendor | Ener Teknoloji |

- Abbreviations

H (Hold): Vendor shall not carry out any fabrication and/ or repair work and any shipment without having inspector's confirmation/comments. Any controls and test without inspector is not allowed. Vendor must notify contractor by E-mail as per defined communication line at least 4 Days before the test date for domestic manufacturers and 7 days for overseas. No deviation is allowed from the above-mentioned issues unless specially approved by Client/Contractor in writing.

W (Witness): Vendor must notify contractor of the dedicated inspection activity at least 4 Days before the test date for domestic manufacturers and 7 days for overseas. Inspector's attendance is not mandatory.

SW (Spot Witness):  At least inspection of 15% of each subjected item shall be done under the supervision of involved inspectors. Relevant inspection notification shall be submitted at the beginning of related activities and in case of any failure, at the first case, inspector's supervision increases to 30% of goods and by the second failure, whole activity shall be witnessed by inspectors.

R (Review): Review Documentation is a point in which inspection result shall be reviewed, but presence of involved party at inspection time is not mandatory

RA (Review Approval): Includes reviewing of all related reports/certificates which vendor shall provide at each step and vendor shall not proceed his fabrication/test unless receiving inspector's approval.

| ROW | Activities | Reference Documents | verifying Document | ACTION |  |  |  |  | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Vendor | PEEDCO | TPA | PJPC |  |  |
| PIM |  |  |  |  |  |  |  |  |  |
| 1 | Pre-Inspection Meeting | Project Specifications and PO and relevant standards | MOM and approved ITP | H | H | R | H |  |  |
| Document Review |  |  |  |  |  |  |  |  |  |
| 2 | Submission of Project documents | Project Specifications and VPIS | Approved Procedures | H | RA | R | R |  |  |
| 3 | Sub Vendor List | Approved Project AVL (MOP, NPC, POGC) | As per approved sub vendor list | H | RA | R | R |  |  |
| Compressor Skid |  |  |  |  |  |  |  |  |  |
| 4 | Compressor Block (Visual, Dimensional, Marking and Document Check) | Approved Datasheet/DWG | MYCOM Certificate and test Report ('- Noise test '- Vibration test '- Performance test '-Hydro test) | H | W | H | R |  |  |
| 5 | MAIN MOTOR - HELMKE GERMANY | Approved Datasheet | HELMKE Certificate and Test Report | H | W | W | R |  |  |
| 6 | PUMP MOTOR-HELMKE GERMANY | Approved Datasheet | HELMKE Certificate and Test Report | H | W | W | R |  |  |
| 7 | Instrument Wiring and Function Test for Instruments | JB Wiring | Approved JB and LCP wiring Diagram | H | W | W | R |  |  |
| 8 | Inspection of Junction Box, Local Panel | Approved Junction Box and LCP Wiring Diagram and PLC Layout Drawing | TEST REPORT PLC FAT TEST PROCEDURE | H | W | W | R |  |  |
| 9 | Compressor Skids including Oil pump, Oil Filter, Piping, Oil Separator, Valves, Instrumentation, etc (Visual, Dimensional, Painting, Marking and Document Check) | Approved Datasheet/DWG | MYCOM Certificate/ Material Certificate and Test Reports | H | W | H | R |  |  |
| 10 | Instrument Wiring and Function Test for Instruments | JB Wiring | Approved JB and LCP wiring Diagram | H | W | W | R |  |  |
| 11 | Packing and Marking | Approved Packing and Marking Procedure | Approved Packing List | H | W | H | R |  |  |
| 12 | Inspection Release Note (IRN) | PO and Approved ITP | Approved Inspection Reports and Approved Packing List | H | H | H | H |  |  |
| PLC |  |  |  |  |  |  |  |  |  |
| 13 | Visual, Dimensional, FAT for PLC | PLC Layout Drawing, IO List, PLC Manual | PLC FAT TEST PROCEDURE | H | W | H | H |  |  |
| 14 | Packing and Marking | Approved Packing and Marking Procedure | Approved Packing List | H | W | H | R |  |  |
| 15 | Inspection Release Note (IRN) | PO and Approved ITP | Approved Packing List | H | H | H | H |  |  |
| Chiller Skid |  |  |  |  |  |  |  |  |  |
| 16 | Shell and Tube Heat Exchanger (Chiller) | Approved GA and Approved Chiller ITP in Table 1 | All sections according to Approved Chiller ITP in Table 1 | - | - | - | - | Refer to Table 1 |  |
| 17 | Valves For Chiller Skid | Approved GA, Approved PID and 3D Model and Applicable Standard | Manufacturer Test Record and traceable original Certificates | H | W | W | R |  |  |
| 18 | Piping For Chiller Skid (Visual, Dimensional, weld check and Hydrotest of pipe spools) | Approved GA, Approved PID and 3D Model | - Traceable original Certificates for Raw Materials -Approved Hydrotest Procedure | H | W | W | R | Note 1 |  |
| 19 | Safety Valves | Approved Data Sheet | Traceable original Certificates | H | W | W | R |  |  |
| 20 | Smaller components within instrumentation routing, such as TUBING and GASKETS and bolting For chiller Skid | Approved GA and Approved Skid Foundation and PID | Traceable original Certificates | H | W | R | R | Note 1, for applicable items |  |
| 21 | Instrumentation | Approved Data Sheet, | Material Certificates, Dimensional And Construction Dwg, Hazardous Area Certificate Calibration Report (3.1 material certificates) | H | W | W | R |  |  |
| 22 | Inspection of Junction Box | Approved Junction Box and LCP Wiring Diagram | TEST REPORT And Certificate | H | W | W | R |  |  |
| 23 | Packing and Marking | Approved Packing and Marking Procedure | Approved Packing List | H | W | H | R |  |  |
| 24 | Inspection Release Note (IRN) | PO and Approved ITP | Approved Inspection Reports and Approved Packing List | H | H | H | H |  |  |
| Air Cooler (Condenser) |  |  |  |  |  |  |  |  |  |
| 25 | Air Cooler (Condenser) | Approved GA and Approved Condenser ITP in Table 2 | All sections according to Approved Condenser ITP in Table 2 | - | - | - | - | Refer to Table 2 |  |
| Documentation |  |  |  |  |  |  |  |  |  |
| 26 | Final Data Book (FDB) | Project Final Data Book Procedure | FDB | H | RA | R | RA |  |  |

Note 1: Original or true copy of EN 10204 3.1 certificate to be issued (if the original/true copy certificate isn’t available, lab test report will be issued).

Table 1: ITP for Chiller

| ROW | Activities | Reference Documents | verifying Document |  | ACTION |  |  |  | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | Vendor | PEEDCO | TPA | PJPC |  |
| Documentation |  |  |  |  |  |  |  |  |  |
| 1 | Sub Vendor List | Approved Project AVL (MOP & NPC &POGC) |  | Approved Sub vendor List | H | RA | R | RA |  |
| 2 | Welding Book (WPS, PQR, NDT Map, NDT Procedure, WQT, NDT Personal cert.) | ASME SEC VIII, V SNT-TC 1A level II |  | Approved Welding Book | H | RA | R | RA |  |
| 3 | Hydrotest Test Procedure | Project Specifications / Applicable standard |  | Approved hydrotest Procedure | H | RA | R | RA |  |
| 4 | Surface preparation and painting | Project Specifications |  | Approved Painting Procedure | H | RA | R | RA |  |
| 5 | Preservation, Packaging, And Shipping Procedure | Project Specifications |  | Approved Packing Procedure | H | RA | R | RA |  |
| Chiller |  |  |  |  |  |  |  |  |  |
| 6 | Raw Material | Approved Datasheet/DWG and relevant standards |  | Material Certificate | H | H | H | R | Note 1 |
| 7 | Cutting | Approved Drawings |  | Inspection Report | R | SW | SW | R |  |
| 8 | Welding | Approved WPS/PQR |  | Inspection Report | H | SW | SW | R |  |
| 9 | Visual And Dimensional Check | Approved Drawings |  | VT&DT Report | H | W | W | R |  |
| 10 | NDT (PT & RTI) | Approved NDT Map and procedure |  | NDT Report | H | W | W | R |  |
| 11 | Fianl Visual and Dimensional Check | Approved Drawings |  | Final VT&DT Report | H | W | W | R |  |
| 12 | Hydro Test tube Side | Approved Hydrotest Procedure |  | Hydrotest Report | H | H | H | W |  |
| 13 | Hydro Test Shell Side | Approved Hydrotest Procedure |  | Hydrotest Report | H | H | H | W |  |
| 14 | Painting and Coating Inspection | Approved Painting Procedure |  | Paint Report | H | W | W | R |  |
| 15 | Name Plate Check | Approved Drawing |  | Inspection Report | H | RA | H | R |  |
| 16 | Packing and Marking | Approved Packing Marking Procedure |  | Approved Packing List | H | W | H | R |  |
| 17 | Inspection Release Note (IRN) | PO and ITP |  | IRN | R | R | H | R |  |

Table 2: ITP for Air Cooler (Condenser)

| ROW | Activities | Reference Documents | verifying Document |  | ACTION |  |  |  | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | Vendor | PEEDCO | TPA | PJPC |  |
| Documentation |  |  |  |  |  |  |  |  |  |
| 1 | Sub Vendor List | Approved Project AVL (MOP & NPC &POGC) |  | Approved Sub vendor List | H | RA | R | RA |  |
| 2 | Welding Book (WPS, PQR, NDT Map, NDT Procedure, WQT, NDT Personal cert.) | ASME SEC VIII, V SNT-TC 1A level II |  | Approved Welding Book | H | RA | R | RA |  |
| 3 | Hydrotest Test Procedure | Project Specifications / Applicable standard |  | Approved hydrotest Procedure | H | RA | R | RA |  |
| 4 | Surface preparation and painting | Project Specifications |  | Approved Painting Procedure | H | RA | R | RA |  |
| 5 | Preservation, Packaging, And Shipping Procedure | Project Specifications |  | Approved Packing Procedure | H | RA | R | RA |  |
| Air Cooler (Condenser) |  |  |  |  |  |  |  |  |  |
| 6 | Raw Material | Approved Datasheet/DWG and relevant standards |  | Material Certificate | H | H | H | R | Note 1 |
| 7 | Cutting | Approved Drawings |  | Inspection Report | R | SW | SW | R |  |
| 8 | Welding | Approved WPS/PQR |  | Inspection Report | H | SW | SW | R |  |
| 9 | Visual And Dimensional Check | Approved Drawings |  | VT&DT Report | H | W | W | R |  |
| 10 | NDT (PT & RTI) | Approved NDT Map and procedure |  | NDT Report | H | W | W | R |  |
| 11 | Fianl Visual and Dimensional Check | Approved Drawings |  | Final VT&DT Report | H | W | W | R |  |
| 12 | Hydro Test | Approved Hydrotest Procedure |  | Hydrotest Report | H | H | H | W |  |
| 13 | Painting and Coating Inspection | Approved Painting Procedure |  | Paint Report | H | W | W | R |  |
| 14 | Name Plate Check | Approved Drawing |  | Inspection Report | H | RA | H | R |  |
| 15 | Packing and Marking | Approved Packing Marking Procedure |  | Approved Packing List | H | W | H | R |  |
| 16 | Inspection Release Note (IRN) | PO and ITP |  | IRN | R | R | H | R |  |