## INDEX
Revision Index
Rev | 00 | 01 | 02 | 03 | 04 | 05 | Rev | 06 | 07 | 08 | 09
Sheet | [6 empty] | Sheet
1 | X
2 | X
3 | X
4
5
6
7
8
9
10

## MTO
No. | Description | Unit A | Unit B | QTY | Engineering Contingency Factor | Spare (Pcs) | Final QTY | Remark
1 | M20S, ISO metric threads to IEC 60423, -Zone 2, IIC, T3, EEx'd', IP65, Suitable for Single wire galvanized round steel armoured cable,Cable: CU/XLPE/SWA/PVC or CU/XLPE/AWA/PVC,Armour clamping type,Gland material: Nickle plated brass,Including PVC shroud, locknut, earth tag & sealing washer to maintain IP65 & over than 85°C | 21 | 21 | 42 | 1.1 | 4 | 50
2 | M20, ISO metric threads to IEC 60423, -Zone 2, IIC, T3, EEx'd', IP65, Suitable for Single wire galvanized round steel armoured cable,Cable: CU/XLPE/SWA/PVC or CU/XLPE/AWA/PVC,Armour clamping type,Gland material: Nickle plated brass,Including PVC shroud, locknut, earth tag & sealing washer to maintain IP65 & over than 85°C | 5 | 5 | 10 | 1.1 | 4 | 15
3 | M20x1.5 Brass Ni-Plated stopping plug with lock-nut |  |  |  |  | 20 | 20

## Unit A
COMPRESSOR RU0001A/B-C-01
No. | Service | Tag No. | Content of signal | SIGNAL Type | IS/NIS | Cable type | Cable size | Gland size | Remarks
1 | Compressor Suction pressure transmitter | PIT-RU0001A-01 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20
2 | Discharge pressure transmitter | PIT-RU0001A-03 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20
3 | Oil header Compressor pressure transmitter | PIT-RU0001A-02 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20
4 | Upstream oil filter pressure transmitter | PIT-RU0001A-05 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20
5 | Downstream oil filter pressure transmitter | PIT-RU0001A-06 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20
6 | Pressure transmitter oil separator | PIT-RU0001A-04 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20
7 | Compressor Suction temperature transmitter | TIT-RU0001A-01 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20
8 | Oil Separator temperature transmitter | TIT-RU0001A-03 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20
9 | Oil header compressor temperature transmitter | TIT-RU0001A-02 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20
10 | Compressor slide valve position sensor | ZE-RU0001A-01 | 3-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20
11 | Chiller level transmitter | LIT-RU0001A-01 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20
12 | Chiller level control valve | LV-RU0001A-01 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20
13 | Oil separator level switch | LS-RU0001A-01 | 24Vdc / **W | Digital | NIS | Type3 | 02Px1.5mm² | M20
14 | Compressor capacity load Return solenoid valve | SOV-RU0001A-01D | 24Vdc / **W | Digital | NIS | Type 2 | 01Px2.5mm² | M20
15 | Compressor capacity unload supply solenoid valve | SOV-RU0001A-01A | 24Vdc / **W | Digital | NIS | Type 2 | 01Px2.5mm² | M20
16 | Compressor capacity load supply solenoid valve | SOV-RU0001A-01C | 24Vdc / **W | Digital | NIS | Type 2 | 01Px2.5mm² | M20
17 | Compressor capacity unload Return solenoid valve | SOV-RU0001A-01E | 24Vdc / **W | Digital | NIS | Type 2 | 01Px2.5mm² | M20
18 | Hot gas solenoid valve | SOV-RU0001A-03 | 24Vdc / **W | Digital | NIS | Type 2 | 01Px2.5mm² | M20
19 | Evaporator oil drain line. | SOV-RU0001A-02 | 24Vdc / **W | Digital | NIS | Type 2 | 01Px2.5mm² | M20
20 | Air Cooler motor 2 vibration switch | VS-RU0001A-01A | 24Vdc / **D | Digital | NIS | Type 2 | 01Px2.5mm² | M20
21 | Air Cooler motor 3 vibration switch | VS-RU0001A-01B | 24Vdc / **D | Digital | NIS | Type 2 | 01Px2.5mm² | M20