## LTLG-RU0001AB-03
#REF!
#REF!
#REF! |  |  |  | #REF! | [6 empty] | Page: 3
#REF! |  |  |  | #REF!
#REF!
GENERAL
1 | Tag No. | LT-RU0001A-03, LG-RU0001A-03,LT-RU0001B-03, LG-RU0001B-03 |  |  |  | 7 | AREA Classification |  |  | Zone 2 IIB T3
2 | Service | EVAPORATOR |  |  |  | 8
3 | Line No. | - |  |  |  | 9
4 | Line Size | Line Schedule |  |  |  | 10
5 | Equipment No. |  |  |  |  | 11
6 | PID No. |  |  |  |  | 12
| GAUGE BODY AND VALVES | [5 empty] | BASIS AND SELECTION
13 | Body Material |  |  | Stainless Steel |  | 56 | Mounting |  |  | LG
14 | Material Detail |  |  | 316 SS |  | 57 | Power Supply From |  |  | 24 Vdc |  | System
15 | Connection Size |  |  | 2" |  | 58 | Accuracy % | Repeatibility |  | ±0.4mm |  | ±0.005%
16 | Connection Layout |  |  | Side-Side |  | 59 | Output signal |  |  | 4-20 mA Hart
17 | Rating | Face |  | CL 300 | RF | 60 | Electrical Protection |  |  | Exia IIC T3
18 | Length Between Connections |  |  | 1220 mm |  | 61 | IP Rating |  |  | IP65
19 | Gasket Material |  |  | Graphite |  | 62 | Zero Adjustment |  |  | External
20 | Float Material |  |  | Titanium |  | 63 | Electrical Connections |  |  | M20 x 1.5
21 | Float Model |  |  |  |  | 64 | Span Adjustable |  |  | External
22 | Bottom Connection |  |  | 2" Flanged |  | 65 | Calibrated Range |  | mm | 0 |  | - | Hold
23 | Bolting and Nutts |  |  | Stainless Steel |  | 66 | DCS Range % |  |  | 0 |  | - | 100
24 | Valves Type |  |  | Ball |  |  | Indicator
25 | Valves Material |  |  | Carbon Steel |  | 67 | Type |  |  | Magnetic Metal Tube
26 | Seat |  |  | Hypatite PTFE |  | 68 | Indicator Elements |  |  | Flappers
27 | Trim Material |  |  | 316 SS |  | 69 | Float Failure indication |  |  | Yes
28 | Drain Connection |  |  | 3/4" Flange |  | 70 | Transparent Front Material |  |  | Fiberglass
29 | Vent Connection |  |  | 3/4" Flange |  | 71 | Indicator Housing Material |  |  | Stainless Steel
30 | Interface Fluid Measures |  |  | Yes |  | 72 | Indication Rail Material |  |  | Stainless Steel
| TRANSMITTER BODY |  |  |  |  | 73 | Graduations |  | % | 0 |  |  | 100
31 | Instrument Function |  |  | Magnetorestrictive |  | 74 | Low Reference Point |  | mm | Hold
32 | Element Type |  |  | Floater |  | 75 | High Reference Point |  | mm | Hold
33 | Element Material |  |  | 316SS Ti |  |  | ACCESSORIES
34 | Housing Material |  |  | Stainless Steel |  | 76 | Indicator |  |  | Digital Local Indicator
35 | Material Detail |  |  | 316SS |  | 77 | Integral Meter Scale |  |  | No
36 | Transmitter Rating |  |  | IP 65 |  | 78 | Mounting Bracket |  |  | No
37 | Overrange Protection |  |  | 130% of Range |  | 79 | Wave / Fluid Stabilizer |  |  | No
38 | Vent | Drain |  | No | No | 80 | Stabilizer Material |  |  | -
39 | Sensor Type |  |  | Core Tube and Fittings |  | 81 | Extension Cable |  |  | No
40 | Sensor Material |  |  | 316L SS |  | 82 | Surge Protection |  |  | No
41 | Bolts Material |  |  | Stainless Steel |  | 83 | Swtich type |  |  | -
42 | Connection Size |  |  | 1/2" |  | 84 | Contact Switch Material |  |  | -
43 | Connection point |  |  | Top |  | 85 | Switch Power Supply or Consumption |  |  | -
| PROCESS DATA |  |  |  |  | 86 | Sunshade |  |  | No
44 | Lower Fluid Name |  |  | PROPANE |  | 87 | Jacket or Internal Tracer |  |  | No
45 | Upper Fluid Name |  |  | PROPANE |  | 88 | Frost Extension |  |  | No
46 | Fluid Phase Lower / Upper |  |  |  | Liquid / Vapor | 89
47 | Pressure Norm |  | bar A |  | 4.7 |  | REQUIREMENTS AND TEST
48 | Temperature Norm / Max |  | °C |  | -0.07 | 90 | NACE Requirments |  |  | No
49 | Density Lower / Upper |  | Kg/m3 |  | 436.9 / 10.22 | 91 | ASME Design |  |  | Yes
50 | Viscosaty Lower / Upper |  | cp |  | 0.059 / 0.0078 | 92 | Material Certification |  |  | 3.1 Material Certificate
51 | Corrosive Agents |  |  | - |  | 93 | Body Hydraulic Test |  |  | Yes
52 | Toxic Agents |  |  | - |  | 94 | Float Hydraulic test |  |  | No
53 | Design Pressure |  | bar G | FV | 22 | 95 | Factory Calibration |  |  | Yes
54 | Design Temp. |  | °C | -45 | 120 | 96 | SIL Requirements |  |  | -
55 | [5 empty] | 97 | NDE |  |  | Manufacturer's Standard
| PURCHASE DATA | [5 empty] | NOTES
98 | Manufacturer |  |  |  |  | 104 | note 1: LG flange connections on Left side note 2: note 3:
99 | Model Number
100 | Smart Plant Code / Glovia Code
101 | Mtr. Requisition
102 | Purchase Order No.
103 | Item Number
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED

## LG-RU0001AB-02
#REF!
#REF!
#REF! |  |  |  | #REF! | [6 empty] | Page: 4
#REF! |  |  |  | #REF!
#REF!
GENERAL
1 | Tag No. | LG-RU0001A-02,LG-RU0001B-02 |  |  |  | 7 | AREA Classification |  |  | Zone 2 IIB T3
2 | Service | RECEIVER HEADER |  |  |  | 8
3 | Line No. | - |  |  |  | 9
4 | Line Size | Line Schedule |  |  |  | 10
5 | Equipment No. |  |  |  |  | 11
6 | PID No. |  |  |  |  | 12
| GAUGE BODY AND VALVES | [5 empty] | BASIS AND SELECTION
13 | Body Material |  |  | SA350-LF2 |  | 56 | Mounting |  |  | LG
14 | Material Detail |  |  | LTCS |  | 57 | Power Supply From |  |  | N/A
15 | Connection Size |  |  | 2" |  | 58 | Accuracy % | Repeatibility
16 | Connection Layout |  |  | Side-Side |  | 59 | Output signal |  |  | N/A
17 | Rating | Face |  | CL 300 | RF | 60 | Electrical Protection |  |  | N/A
18 | Length Between Connections |  |  | 762 mm |  | 61 | IP Rating |  |  | 65
19 | Drain Connection |  |  | 3/4" Flange |  | 62 | Zero Adjustment |  |  | N/A
20 | Vent Connection |  |  | 3/4" Flange |  | 63 | Electrical Connections |  |  | N/A
21 | Trim |  |  | 316L SS |  | 64 | Span Adjustable |  |  | N/A
22 | Bonnet |  |  | PACKING NUT / TEFLON PACKING |  | 65 | Calibrated Range |  | mm
23 | [5 empty] | 66 | DCS Range %
24 | [6 empty] | Indicator
25 | [5 empty] | 67 | Type |  |  | Reflex
26 | [5 empty] | 68 | size |  |  | 7 (VTC)
27 | [5 empty] | 69 | No. of section |  |  | 2 (VTC)
28 | [5 empty] | 70
29 | [5 empty] | 71
30 | [5 empty] | 72
| TRANSMITTER BODY |  |  |  |  | 73
31 | Instrument Function |  |  | No |  | 74
32 | Element Type |  |  |  |  | 75
33 | Element Material | [5 empty] | ACCESSORIES
34 | Housing Material |  |  |  |  | 76 | Indicator |  |  | N/A
35 | Material Detail |  |  |  |  | 77 | Integral Meter Scale
36 | Transmitter Rating |  |  |  |  | 78 | Mounting Bracket
37 | Overrange Protection |  |  |  |  | 79 | Wave / Fluid Stabilizer
38 | Vent | Drain |  |  |  | 80 | Stabilizer Material
39 | Sensor Type |  |  |  |  | 81 | Extension Cable
40 | Sensor Material |  |  |  |  | 82 | Surge Protection
41 | Bolts Material |  |  |  |  | 83 | Swtich type
42 | Connection Size |  |  |  |  | 84 | Contact Switch Material
43 | Connection point |  |  |  |  | 85 | Switch Power Supply or Consumption
| PROCESS DATA |  |  |  |  | 86 | Sunshade
44 | Lower Fluid Name |  |  | PROPANE |  | 87 | Jacket or Internal Tracer
45 | Upper Fluid Name |  |  | PROPANE |  | 88 | Frost Extension
46 | Fluid Phase Lower / Upper |  |  |  | Liquid / Vapor | 89
47 | Pressure Norm |  | bar A |  | 19.7 |  | REQUIREMENTS AND TEST
48 | Temperature Norm / Max |  | °C |  | 56.32 | 90 | NACE Requirments |  |  | No
49 | Density Lower / Upper |  | Kg/m3 |  | 436.9 / 43.38 | 91 | ASME Design |  |  | Yes
50 | Viscosaty Lower / Upper |  | cp |  | 0.059 / 0.0106 | 92 | Material Certification |  |  | 3.1 Material Certificate
51 | Corrosive Agents |  |  | - |  | 93 | Body Hydraulic Test |  |  | Yes
52 | Toxic Agents |  |  | - |  | 94 | Float Hydraulic test |  |  | No
53 | Design Pressure |  | bar G | FV | 22 | 95 | Factory Calibration |  |  | Yes
54 | Design Temp. |  | °C | -45 | 120 | 96 | 1200 |  |  | -
55 | [5 empty] | 97 | NDE |  |  | Manufacturer's Standard
| PURCHASE DATA | [5 empty] | NOTES
98 | Manufacturer |  |  |  |  | 104 | note 1: LG flange connections on Left side note 2: note 3:
99 | Model Number
100 | Smart Plant Code / Glovia Code
101 | Mtr. Requisition
102 | Purchase Order No.
103 | Item Number
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED

## LS-RU0001A-01
#REF!
#REF!
#REF! |  |  |  | #REF! | [6 empty] | Page: 4
#REF! |  |  |  | #REF!
#REF!
GENERAL
1 | Tag No. | LS-RU0001A-01, LS-RU0001B-01 |  |  |  | 7 | AREA Classification |  |  | Zone 2 IIB T3
2 | Service | Oil Separator |  |  |  | 8
3 | Line No. | - |  |  |  | 9
4 | Line Size | Line Schedule |  |  |  | 10
5 | Equipment No. | RU0001A-D-01 |  |  |  | 11
6 | PID No. |  |  |  |  | 12
| LEVEL SWITCH | [5 empty] | BASIS AND SELECTION
13 | Body Material |  |  | Stainless Steel |  | 56 | Mounting
14 | Material Detail |  |  | 316 SS |  | 57 | Power Supply From |  |  | 24 Vdc
15 | Connection Size |  |  | 3/4" NPT |  | 58 | Accuracy % | Repeatibility
16 | Connection Layout |  |  | Side |  | 59 | Output signal |  |  | DRY CONTACT
17 | Rating | Face |  |  |  | 60 | Electrical Protection |  |  | Exd
18 | Gasket Material |  |  | Graphite |  | 61 | IP Rating |  |  | 65
19 | Bolting and Nutts |  |  | Stainless Steel |  | 62 | Electrical Connections |  |  | M20 *1.5
20 | [5 empty] | 63
21 | [5 empty] | 64
22 | [5 empty] | 65
23 | [5 empty] | 66
24 | [6 empty] | Indicator
25 | [5 empty] | 67 | Type |  |  | N/A
26 | [5 empty] | 68 | Indicator Elements
27 | [5 empty] | 69 | Float Failure indication
28 | [5 empty] | 70 | Transparent Front Material
29 | [5 empty] | 71 | Indicator Housing Material
30 | [5 empty] | 72 | Indication Rail Material
| TRANSMITTER BODY |  |  |  |  | 73 | Graduations |  | %
31 | Instrument Function |  |  | Low level detection |  | 74 | Low Reference Point |  | mm
32 | Element Type |  |  | Vibration |  | 75 | High Reference Point |  | mm
33 | Element Material | [5 empty] | ACCESSORIES
34 | Housing Material |  |  |  |  | 76 | Indicator |  |  | No
35 | Material Detail |  |  |  |  | 77 | Integral Meter Scale |  |  | No
36 | Transmitter Rating |  |  | 5~100 C |  | 78 | Mounting Bracket |  |  | No
37 | Overrange Protection |  |  |  |  | 79 | Wave / Fluid Stabilizer |  |  | No
38 | Vent | Drain |  | N/A | N/A | 80 | Stabilizer Material |  |  | -
39 | Sensor Type |  |  |  |  | 81 | Extension Cable |  |  | No
40 | Sensor Material |  |  |  |  | 82 | Surge Protection |  |  | No
41 | Bolts Material |  |  |  |  | 83 | Swtich type |  |  | -
42 | Connection Size |  |  | 3/4" NPT |  | 84 | Contact Switch Material |  |  | -
43 | Connection point |  |  |  |  | 85 | Switch Power Supply or Consumption |  |  | -
| PROCESS DATA |  |  |  |  | 86 | Sunshade |  |  | No
44 | Lower Fluid Name |  |  | OIL |  | 87 | Jacket or Internal Tracer |  |  | No
45 | Upper Fluid Name |  |  |  |  | 88 | Frost Extension |  |  | No
46 | Fluid Phase Lower / Upper |  |  |  | Liquid | 89
47 | Pressure Norm |  | bar A |  | 20.2 |  | REQUIREMENTS AND TEST
48 | Temperature Norm / Max |  | °C |  | 73.5 | 90 | NACE Requirments |  |  | No
49 | Density Lower / Upper |  | Kg/m3 |  | 1005 | 91 | ASME Design |  |  | No
50 | Viscosaty Lower / Upper |  | cp |  | 12 | 92 | Material Certification |  |  | 3.1 Material Certificate
51 | Corrosive Agents |  |  | - |  | 93 | Body Hydraulic Test |  |  | Yes
52 | Toxic Agents |  |  | - |  | 94 | Float Hydraulic test |  |  | No
53 | Design Pressure |  | bar G | -1 | 22 | 95 | Factory Calibration |  |  | Yes
54 | Design Temp. |  | °C | 5 | 100 | 96 | SIL Requirements |  |  | -
55 | [5 empty] | 97 | NDE |  |  | Manufacturer's Standard
| PURCHASE DATA | [5 empty] | NOTES
98 | Manufacturer |  |  |  |  | 104 | 1)Fork level switch is not acceptable 2)IEC standard to be followed
99 | Model Number
100 | Smart Plant Code / Glovia Code
101 | Mtr. Requisition
102 | Purchase Order No.
103 | Item Number
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED
PROPERTY OF TECHNIP KTI SpA TO BE RETURNED UPON REQUEST AND USED ONLY IN REFERENCE TO CONTRACT OR PROPOSALS OF THIS COMPANY. REPRODUCTION OF THIS PRINT OR UNAUTHORIZED USE OF PATENDED OR PATENTABLE FEATURES DISCLOSED HEREON IS PROHIBITED