## Valve List-RU0001A
Item | P&ID No. | Line Number | Tag No. | Name | Maker | Model No. (DWG NO.) | Valve Type | Body /Trim material | Connection |  |  | Fluid | Design Condition |  | Operating Condition |  | Insulation | QTY | Total | Pipe Class | Remark | Note |  | Rev.
[9 empty] | Size | Standard | Type |  | Press. (bar G) | Temp (℃) | (bar G) Press. | Temp (℃)
1 | EI027-HSE-VD-PR-PID-0002 Sht 5/7 | 1"-PR-RU0001A16-Ml3R1-N | GLO-RU0001A02 |  |  |  | GLOBE VALVE | LTCS/SS | 25mm | 300# | Flanged | Refrigerant | FV/22 | -45 ~ 120 | 18.8 | 73.5 | N | 1 | 1 | ML3R1
2 | EI027-HSE-VD-PR-PID-0002 Sht 5/7 | 1"-PR-RU0001A13-ML3R1-N | CHV-RU0001A04 |  |  |  | CHECK VALVE | LTCS/SS | 25mm | 300# | Flanged | Refrigerant | FV/22 | -45 ~ 120 | 18.7 | 56.32 | N | 1 | 1 | ML3R1 |  |  | Both Swing type or Piston Type are acceptable
3 | EI027-HSE-VD-PR-PID-0002 Sht 6/7 | 1 1/2"-PR-RU0001A06-ML3R1-N | GLO-RU0001A03 |  |  |  | GLOBE VALVE | LTCS/SS | 25mm | 300# | Flanged | Refrigerant | FV/22 | -45 ~ 120 | 18.7 | 56.32 | Y | 1 | 1 | ML3R1 | With Extended stem
4 | EI027-HSE-VD-PR-PID-0002 Sht 6/7 | 6"-PR-RU0001A01-ML3R1-C | GLO-RU0001A04 |  |  |  | GLOBE VALVE | LTCS/SS | 150mm | 300# | Flanged | Refrigerant | FV/22 | -45 ~ 120 | 3.7 | -0.17 | Y | 1 | 1 | ML3R1 | With Extended stem
5 | EI027-HSE-VD-PR-PID-0002 Sht 3/7 | 2"-PR-RU0001A04-ML3R1-P | CHV-RU0001A03 |  |  |  | CHECK VALVE | CS/SS | 50mm | 300# | RF Flanged, Wafer Type | Refrigerant | FV/22 | -29 ~ 120 | 18.8 | 73.5 | N | 1 | 1 | MC3R1 | INLINE, Dual Flapper |  | Disk Material: SS Body Material: CS SEAL / SPRING / STOP PIN: CS / Inconel / 316SS STYLE: Vertical Swing type is first priority
6 | EI027-HSE-VD-PR-PID-0002 Sht 3/7 | TUBING | SG-RU0001A01 |  |  |  | Sight Glass | SS316/SS316 | 3/8" | NPT-F | Thraded | Lube Oil | FV/22 | 120 | 18.8 | 73.5 | N | 1 | 1 | Tubing
7 | EI027-HSE-VD-PR-PID-0002 Sht 6/7 | TUBING | SG-RU0001A02 |  |  |  | Sight Glass | SS316/SS316 | 3/8" | NPT-F | Thraded | Refrigerant | FV/22 | -45 ~ 120 | 18.8 | -0.17 | N | 1 | 1 | Tubing
8 | EI027-HSE-VD-PR-PID-0002 Sht 3/7 | TUBING | Spare |  |  |  | Sight Glass | SS316/SS316 | 3/8" | NPT-F | Thraded | Lube Oil | FV/22 | 120 | 18.8 | 73.5 | N | 1 | 2 | Tubing
9 | EI027-HSE-VD-PR-PID-0002 Sht 6/7 | TUBING | Spare |  |  |  | Sight Glass | SS316/SS316 | 1/2" | NPT-F | Thraded | Refrigerant | FV/22 | -45 ~ 120 | 18.8 | -0.17 | N | 3 | 6 | Tubing
10 | EI027-HSE-VD-PR-PID-0002 Sht 3/7 | Tubing | YST-RU0001A01 |  |  |  | Strainer | CS/SS | 3/8" | NPT-F 300# | Thraded (FPT) | Lube Oil | FV/22 | -29 ~ 120 | 18.8 | 73.5 | N | 1 | 1 | Tubing |  |  | Mesh Screen Material: SS316 Mesh Size: 90
11 | EI027-HSE-VD-PR-PID-0002 Sht 6/7 | Tubing | YST-RU0001A02 |  |  |  | Strainer | LTCS/SS | 1/2" | NPT-F 300# | Thraded (FPT) | Refigerant | FV/22 | -45 ~ 120 | 3.7 | -0.17 | N | 1 | 1 | Tubing |  |  | Mesh Screen Material: SS316 Mesh Size: 90

## Valve List-RU0001B
Item | P&ID No. | Line Number | Tag No. | Name | Maker | Model No. (DWG NO.) | Valve Type | Body /Trim material | Connection |  |  | Fluid | Design Condition |  | Operating Condition |  | Insulation | QTY | Total | Pipe Class | Remark | Note |  | Rev.
[9 empty] | Size | Standard | Type |  | Press. (bar G) | Temp (℃) | (bar G) Press. | Temp (℃)
1 | EI027-HSE-VD-PR-PID-0002 Sht 5/7 | 1"-PR-RU0001B16-Ml3R1-N | GLO-RU0001B02 |  |  |  | GLOBE VALVE | LTCS/SS | 25mm | 300# | Flanged | Refrigerant | FV/22 | -45 ~ 120 | 18.8 | 73.5 | N | 1 | 1 | ML3R1
2 | EI027-HSE-VD-PR-PID-0002 Sht 5/7 | 1"-PR-RU0001B13-ML3R1-N | CHV-RU0001B04 |  |  |  | CHECK VALVE | LTCS/SS | 25mm | 300# | Flanged | Refrigerant | FV/22 | -45 ~ 120 | 18.7 | 56.32 | N | 1 | 1 | ML3R1 |  |  | Both Swing type or Piston Type are acceptable
3 | EI027-HSE-VD-PR-PID-0002 Sht 6/7 | 1 1/2"-PR-RU0001B06-ML3R1-N | GLO-RU0001B03 |  |  |  | GLOBE VALVE | LTCS/SS | 25mm | 300# | Flanged | Refrigerant | FV/22 | -45 ~ 120 | 18.7 | 56.32 | Y | 1 | 1 | ML3R1 | With Extended stem
4 | EI027-HSE-VD-PR-PID-0002 Sht 6/7 | 6"-PR-RU0001B01-ML3R1-C | GLO-RU0001B04 |  |  |  | GLOBE VALVE | LTCS/SS | 150mm | 300# | Flanged | Refrigerant | FV/22 | -45 ~ 120 | 3.7 | -0.17 | Y | 1 | 1 | ML3R1 | With Extended stem
5 | EI027-HSE-VD-PR-PID-0002 Sht 3/7 | 2"-PR-RU0001B04-ML3R1-P | CHV-RU0001B03 |  |  |  | CHECK VALVE | CS/SS | 50mm | 300# | RF Flanged, Wafer Type | Refrigerant | FV/22 | -29 ~ 120 | 18.8 | 73.5 | N | 1 | 1 | MC3R1 | INLINE, Dual Flapper |  | Disk Material: SS Body Material: CS SEAL / SPRING / STOP PIN: CS / Inconel / 316SS STYLE: Vertical Swing type is first priority
6 | EI027-HSE-VD-PR-PID-0002 Sht 3/7 | TUBING | SG-RU0001B01 |  |  |  | Sight Glass | SS316/SS316 | 3/8" | NPT-F | Thraded | Lube Oil | FV/22 | 120 | 18.8 | 73.5 | N | 1 | 1 | Tubing
7 | EI027-HSE-VD-PR-PID-0002 Sht 6/7 | TUBING | SG-RU0001B02 |  |  |  | Sight Glass | SS316/SS316 | 3/8" | NPT-F | Thraded | Refrigerant | FV/22 | -45 ~ 120 | 18.8 | -0.17 | N | 1 | 1 | Tubing
8 | EI027-HSE-VD-PR-PID-0002 Sht 3/7 | TUBING | Spare |  |  |  | Sight Glass | SS316/SS316 | 3/8" | NPT-F | Thraded | Lube Oil | FV/22 | 120 | 18.8 | 73.5 | N | 1 | 2 | Tubing
9 | EI027-HSE-VD-PR-PID-0002 Sht 6/7 | TUBING | Spare |  |  |  | Sight Glass | SS316/SS316 | 1/2" | NPT-F | Thraded | Refrigerant | FV/22 | -45 ~ 120 | 18.8 | -0.17 | N | 3 | 6 | Tubing
10 | EI027-HSE-VD-PR-PID-0002 Sht 3/7 | Tubing | YST-RU0001B01 |  |  |  | Strainer | CS/SS | 3/8" | NPT-F 300# | Thraded (FPT) | Lube Oil | FV/22 | -29 ~ 120 | 18.8 | 73.5 | N | 1 | 1 | Tubing |  |  | Mesh Screen Material: SS316 Mesh Size: 90
11 | EI027-HSE-VD-PR-PID-0002 Sht 6/7 | Tubing | YST-RU0001B02 |  |  |  | Strainer | LTCS/SS | 1/2" | NPT-F 300# | Thraded (FPT) | Refigerant | FV/22 | -45 ~ 120 | 3.7 | -0.17 | N | 1 | 1 | Tubing |  |  | Mesh Screen Material: SS316 Mesh Size: 90