## Table 1
[9 empty] | EFFECT | SERVICE | DESCRIPTION | OPERATING CONDITION | UNITS | TRIP | ALARM | ALAM | TRIP |  |  | PID SETPOINT |  | INSTRUMENT RANGE |  |  | INSTRUMENT OUTPUT | [7 empty] | -
SETPOINT LIST | [6 empty] | MAYEKAWA DOC.: | PR200
CLIENT: | [6 empty] | DELTA
PO. No.: | [6 empty] | DELTA-MME-2022-180-001
LOCATION: | [6 empty] | IRAQ
SERVICE: | [6 empty] | PROPYLENE REFRIGERATION PACKAGE
UNIT: | [6 empty] | RU-60001
REV | DATE | PREPARED BY |  | CHECKED BY |  |  | DESCRIPTION
0 | 2023-02-01 | S |  | I |  |  | ORIGINAL RELEASE
[10 empty] | CONDITION |  |  |  | LL | L | H | HH |  |  |  |  | LO | HI | UNITS
INSTRUMENT
INTERLOCK | INPUT TYPE | SERVICE | [5 empty] | TAG No.
|  | P&ID |  |  |  | DESCRIPTION | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22
|  | MAYEKAWA |  |  | CLIENT
1 | AI | EI027-HSE-VD-PR-PID-002 |  | 2 |  | COMPRESSOR SUCTION PRESSURE |  | PIT- | RU0001A-01 |  | 1 | 1: 3.65; 2: BarG; 3: 3; 4: 3.2; 5: 5; 6: 5.4; 9: N/A; 11: 4; 12: 20; 13: mA
2 | AI | EI027-HSE-VD-PR-PID-002 |  | 3 |  | COMPRESSOR DISCHARGE PRESSURE |  | PIT- | RU0001A-03 |  | 2 | 1: 19.2; 2: BarG; 3: 17.5; 4: 9; 5: 20.9; 6: 19.8; 9: N/A; 11: 4; 12: 20; 13: mA
3 | AI | MPE-004 | 20001 | -1 |  | COMPRESSOR SUCTION TEMPERATURE |  | TIT- | RU600101 |  | 3 | 1: -3.96; 2: °C; 4: -8; 5: 3; 9: N/A; 11: 4; 12: 20; 13: mA
4 | AI | EI027-HSE-VD-PR-PID-002 |  | 3 |  | COMPRESSOR DISCHARGE TEMPERATURE |  | TIT- | RU0001A-03 |  | 4 | 1: 73.5; 2: °C; 3: 69.2; 4: 70.4; 5: 85; 6: 90; 9: N/A; 11: 4; 12: 20; 13: mA
5 | AI | EI027-HSE-VD-PR-PID-002 |  | 2 |  | LUBE OIL SUPPLY PRESSURE |  | PIT- | RU0001A-02 |  | 5 | 1: 21.5; 2: BarG; 9: N/A; 11: 4; 12: 20; 13: mA
6 | AI | EI027-HSE-VD-PR-PID-002 |  | 2 |  | LUBE OIL DIFFERENTIAL PRESSURE-Calculated - NOTE 6 |  | PDI- | RU0001A-01 |  | 6 | 1: 2; 2: Bar; 3: 1; 4: 1.5; 5: 4.5; 9: N/A; 11: N/A; 12: N/A; 13: mA
7 | AI | EI027-HSE-VD-PR-PID-002 |  | 2 |  | LUBE OIL SUPPLY TEMPERATURE |  | TIT- | RU0001A-02 |  | 7 | 1: 60; 2: °C; 4: 20; 5: 65; 6: 68; 9: N/A; 11: 4; 12: 20; 13: mA
8 | AI | EI027-HSE-VD-PR-PID-002 |  | 4 |  | OIL FILTER SUPPLY PRESSURE |  | PIT- | RU0001A-06 |  | 8 | 1: 18.7; 2: BarG; 9: N/A; 11: 4; 12: 20; 13: mA
9 | AI | EI027-HSE-VD-PR-PID-002 |  | 4 |  | OIL FILTER DIFFERENTIAL PRESSURE-Calculated - NOTE 7 |  | PDI- | RU0001A-03 |  | 9 | 1: 0.2; 2: Bar; 5: 0.8; 9: N/A; 11: N/A; 12: N/A; 13: mA
10 | AI | EI027-HSE-VD-PR-PID-002 |  | 3 |  | OIL HEATER TEMPERATURE |  | TS- | RU0001A-01B |  | 10 | 1: 73.5; 2: °C; 3: 60; 4: 120; 6: 120; 9: N/A; 11: 4; 12: 20; 13: mA
11 | AI | MPE-004 | 20001 | -1 |  | COALESCER DISCHARGE PRESSURE |  | PIT- | RU600114 |  | 11 | 1: 19.27; 2: BarG; 9: N/A; 11: 4; 12: 20; 13: mA
12 | AI | EI027-HSE-VD-PR-PID-002 |  | 3 |  | OIL SEPARATOR DIFFERENTIAL PRESSURE-Calculated - NOTE 2 |  | PDI- | RU0001A-02 |  | 12 | 1: 0.3; 2: Bar; 5: 0.5; 9: N/A; 11: N/A; 12: N/A; 13: mA
13 | AI | EI027-HSE-VD-PR-PID-002 |  | 2 |  | COMPRESSOR MOTOR AMPERAGE |  | II- | RU0001A-01 |  | 13 | 2: Amp; 5: 105; 6: 115; 9: N/A; 11: 4; 12: 20; 13: mA
14 | AI | MPE-004 | 20001 | -1 |  | COMPRESSOR CASING VIBRATION |  | VI- | RU600101 |  | 14 | 1: 7.1; 2: mm/sec; 5: 14.2; 6: 21.3; 9: N/A; 11: 4; 12: 20; 13: mA
15 | AI | MPE-004 | 20001 | -1 |  | COMPRESSOR MOTOR DE BEARING TEMPERATURE-NOTE 5 |  | TI- | RU600111 |  | 15 | 1: 80; 2: °C; 5: 115; 6: 120; 9: N/A; 11: 4; 12: 20; 13: mA
16 | AI | MPE-004 | 20001 | -1 |  | COMPRESSOR MOTOR NDE BEARING TEMPERATURE-NOTE 5 |  | TI- | RU600112 |  | 16 | 1: 80; 2: °C; 5: 115; 6: 120; 9: N/A; 11: 4; 12: 20; 13: mA
17 | AI | EI027-HSE-VD-PR-PID-002 |  | 2 |  | COMPRESSOR MOTOR WINDINGG TEMPERATURE - NOTE 3 |  | PTC- | RU0001A-13 |  | 17 | 1: 125; 2: °C; 6: 150; 9: N/A; 13: RTD
18 | AI | EI027-HSE-VD-PR-PID-002 |  | 2 |  | COMPRESSOR MOTOR WINDINGG TEMPERATURE - NOTE 3 |  | PTC- | RU0001A-14 |  | 18 | 1: 125; 2: °C; 6: 150; 9: N/A; 13: RTD
19 | AI | EI027-HSE-VD-PR-PID-002 |  | 2 |  | COMPRESSOR MOTOR WINDINGG TEMPERATURE - NOTE 3 |  | PTC- | RU0001A-15 |  | 19 | 1: 125; 2: °C; 6: 150; 9: N/A; 13: RTD
20 | AI | MPE-004 | 20001 | -1 |  | COMPRESSOR MOTOR WINDINGG TEMPERATURE - NOTE 3 |  | TI- | RU600116 |  | 20 | 1: 100; 2: °C; 5: 140; 6: 150; 9: N/A; 13: RTD
21 | AI | MPE-004 | 20001 | -1 |  | COMPRESSOR MOTOR WINDINGG TEMPERATURE - NOTE 3 |  | TI- | RU600117 |  | 21 | 1: 100; 2: °C; 5: 140; 6: 150; 9: N/A; 13: RTD
22 | AI | MPE-004 | 20001 | -1 |  | COMPRESSOR MOTOR WINDINGG TEMPERATURE - NOTE 3 |  | TI- | RU600118 |  | 22 | 1: 100; 2: °C; 5: 140; 6: 150; 9: N/A; 13: RTD
23 | AI | EI027-HSE-VD-PR-PID-002 |  | 3 |  | OIL HEATER |  | TS- | RU0001A-01B |  | 23 | 1: 73.5; 2: °C; 6: 100
24 | AI | EI027-HSE-VD-PR-PID-002 |  | 3 |  | OIL SEPARATOR LEVEL |  | LS- | RU0001A-01 |  | 24 | 1: 50; 2: %; 4: See N9; 9: N/A; 11: 4; 12: 20; 13: mA
25 | AI | EI027-HSE-VD-PR-PID-002 |  | 6 |  | CHILLER LEVEL |  | LIT- | RU0001A-01 |  | 25 | 1: 60; 2: %; 3: 10%; 4: 20%; 5: 80%; 6: 90%; 9: N/A; 11: 4; 12: 20; 13: mA
26 | AI | MPE-004 | 20001 | -2 |  | CHILLER PROCESS OUTLET TEMPERATURE |  | TI- | RU600105 |  | 26 | 1: 2; 2: °C; 3: -5; 4: -1; 5: 3; 6: 9; 9: N/A; 11: 4; 12: 20; 13: mA
27 | AI | EI027-HSE-VD-PR-PID-002 |  | 2 |  | COMPRESSOR SLIDE VALVE CONTROL PRESSURE |  | PIC- | RU0001A-01 |  | 27 | 1: 21.5; 2: BarG; 9: 4.65; 11: 4; 12: 20; 13: mA; 14: PYI-RU0001A-01
28 | AI | MPE-004 | 20001 | -1 |  | COMPRESSOR RECYCLE VALVE CONTROL PRESSURE |  | PIC- | RU600101 |  | 28 | 1: 3.9; 2: BarG; 9: 3.9; 11: 4; 12: 20; 13: mA; 14: PYI-RU600101
29 | AI | MPE-004 | 20001 | -2 |  | CHILLER PROCESS OUTLET TEMPERATURE |  | TIC- | RU600105 |  | 29 | 1: 2; 2: °C; 9: 2; 11: 4; 12: 20; 13: mA; 14: TYI-RU600105
30 | AI | EI027-HSE-VD-PR-PID-002 |  | 6 |  | CHILLER LEVEL - NOTE 4 |  | LIC- | RU0001A-01 |  | 30 | 1: 60; 2: %; 9: 60%; 11: 4; 12: 20; 13: mA; 14: LYI-RU0001A-01
31 | [10 empty] | 31
32 | AI | EI027-HSE-VD-PR-PID-002 |  | 5 |  | CONDENSER MOTOR A VIBRATION |  | VS- | RU0001A-01A |  | 32 | bar: 1 to 2; 6
33 | AI | EI027-HSE-VD-PR-PID-002 |  | 5 |  | CONDENSER MOTOR B VIBRATION |  | VS- | RU0001A-01B |  | 33 | bar: 1 to 2; 6
34 | [10 empty] | 34
35 | [10 empty] | 35
36 | [10 empty] | 36
37 | [10 empty] | 37
38 | [10 empty] | 38
39 | [10 empty] | 39
NOTES: 1 FOR DETAILED OPERATING CONDITIONS REFER TO MPG009-20085 PROCESS FLOW DIAGRAM. 2 OIL SEPARATOR DIFFERENTIAL PRESSURE READING IS TAKING AS THE DIFFERENCE BETWEEN SIGNALS FOR PT-RU0001A-03 AND PT-RU0001A-04. 3 MOTOR WINDING RTD ARE DIRECTLY WIRED TO MCC FROM JUNCTION BOX LOCATED ON THE MOTOR. 4 CALIBRATION RANGE IS BASED ON NOZZLE TO NOZZLE (100%) WHERE THE SEALS ARE CONNECTED. 5 MOTOR BEARING RTD ARE WIRED TO THE UCP, WHERE 4-20 mA CONVERTERS ARE INSTALLED. 6 OIL SUPPLY DIFFERENTIAL PRESSURE READING IS TAKING AS THE DIFFERENCE BETWEEN SIGNALS FOR PT-RU0001A-02 AND PT-RU0001A-03. 7 OIL FILTER DIFFERENTIAL PRESSURE READING IS TAKING AS THE DIFFERENCE BETWEEN SIGNALS FOR PT-RU0001A-05 AND PT-RU0001A-06. 8 THIS DOCUMENT IS PREPARED FOR RU-0001A AND IS TYPICAL FOR RU-0001B WITH CHANGING SUFFIX OF ALL TAG NUMBERS FROM "A" TO "B". E.G. PG-RU0001B-01 9 Level swith provides a contact when healthy condition is present ( oil is location above the sensor)