## CAUSE AND EFFECT CHART
#REF!
#REF!
Page: 1 of 2
[8 empty] | EFFECT | Rev.
[9 empty] | NOTES |  |  | 5 |  |  |  | 7
[9 empty] | CUSTOMER P&ID No. EI027-HSE-VD-PR-PID-002 (SHEET No.) | 7 | 7 | 7 | 7 | 7 | 6 | 2 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 5 | 5
[9 empty] | ACTION | Immediate stop of compressor | Immediate stop of oil pump RU0001A-P-01 | Immediate stop of separator oil heater | Sequential stop of compressor | Sequential stop of oil pump | Initializing to stand-by position | Initializing to stand-by position | Initializing to stand-by position | Unloading slide valve before stop oil pumps | Forbid load command of compressor capacity control | Forced unloading compressor capacity control | Alarm indication on LCP (common) and HMI (indivisual) | Trip indication on LCP (common) and HMI (indivisual) | Status indication on HMI (indivisual) | Immediate stop of condenser fan A | Immediate stop of condenser fan B
[9 empty] | DESCRIPTION | Compressor shutdown trip | Oil pump RU0001A-P-01 shutdown trip | Separator oil heater stop | Controlled stop compressor | Controlled stop oil pumps | Stop controlling Control valves | Close compresor capacity control SOV | Closing solenoid valves Refrigeration package | Return to home position command | Hold limitter of compressor capacity control | Unload limitter of compressor capacity control | Alarm indication | Trip signal to plant (Package shut down /Trip) | Status indication | Aircooler fan A shutdown tip | Aircooler fan B shutdown tip
[9 empty] | EQUIPMENT TAG No. | RU0001A-M-01 | RU0001A-P-01 | RU0001A-H-01 | RU0001A-M-01 | RU0001A-P-01 | LCV-RU0001A-01 | SOV-RU0001A-01A/B/C/D | SOV-RU0001A-02/SOV-RU0001A-03 | RU0001A-C-01 | RU0001A-C-01 | RU0001A-C-01 | XA-RU0001A-01 | XA-RU0001A-02 | Tag Nr N/A | RU0001A-M-02 | RU0001A-M-03
CAUSE
NOTES | CUSTOMER P&ID No. EI027-HSE-VD-PR-PID-002 (SHEET No.) | INSTRUMENT | DESCRIPTION | CLASSIFICATION | CONDITION OF ACTIVATION | PLACE OF GENERATION SOURCE | TAG No. | [19 empty] | Rev.
9 | 7 | HSS-RU0001A-01 | Emergency stop (local panel RU0001A-LCP-01) | Unit trip | 1 | LCP | HSSHH-RU0001A-01 |  | 1 | X | X | X |  |  | X | X | X |  |  |  |  | X |  | X | X | 1
9 | 7 | ESD-RU0001A-01 | ESD emergency shutdown | Unit trip | 1 | UCP | ESDHH-RU0001A-01 |  | 2 | X | X | X |  |  | X | X | X |  |  |  |  | X |  | X | X | 2
|  |  | ESD emergency shutdown CLIENT | Unit trip | 1 | UCP | ESDHH-RU0001A-02 |  | 3 | X | X | X |  |  | X | X | X |  |  |  |  | X |  | X | X | 3
| 2 | PIT-RU0001A-01 | Compressor Suction pressure low low | Unit trip | 1,3 | UCP | PISALL--RU0001A-01 |  | 4 | X |  |  |  | X | X |  | X | X |  |  |  | X |  |  |  | 4
| 2 | PIT-RU0001A-01 | Compressor Suction pressure high high | Unit trip | 1,3 | UCP | PISAHH--RU0001A-01 |  | 5 | X |  |  |  | X | X |  | X | X |  |  |  | X |  |  |  | 5
| 3 | PIT-RU0001A-03 | Compressor Discharge pressure high high | Unit trip | 1 | UCP | PISAHH--RU0001A-03 |  | 6 | X |  |  |  | X | X |  | X | X |  |  |  | X |  |  |  | 6
| 2 | PDI-RU0001A-01 | Compressor Oil supply header diff. press. low low | Unit trip | 1,3,4 | UCP | PDISALL-RU0001A-01 |  | 7 | X | X |  |  |  | X | X | X |  |  |  |  | X |  |  |  | 7
| 2 | TIT-RU0001A-02 | Oil header temperature High High | Unit trip | 1 | UCP | TISAHH-RU0001A-02 |  | 8 | X |  |  |  |  | X | X | X |  |  |  |  | X |  |  |  | 8
| 4 | PDI-RU0001A-03 | Oil Filter differential pressure high high | Unit trip | 1 | UCP | PDISAHH-RU0001A-03 |  | 9 | X |  |  |  | X | X | X | X |  |  |  |  | X |  |  |  | 9
10 | 3 | TIT-RU0001A-03 | Compressor Discharge temperature high high | Unit trip | 1 | UCP | TISAHH-RU0001A-03 |  | 10 | X |  |  |  | X | X | X | X | X |  |  |  | X |  |  |  | 10
| 2 | XL-RU0001A-01 | Compressor motor operation failure | Unit trip | 1,7 | MCC | XLHH-RU0001A-01 |  | 11 | X |  |  |  | X | X | X | X | X |  |  |  | X |  |  |  | 11
3.6 | 2 | II-RU0001A-01 | Compressor motor high High Amperage | Unit trip | 1 | MCC | IISAHH-RU0001A-01 |  | 12 | X |  |  |  | X | X | X | X | X | [7 empty] | 12
1,3,9 | 2 | XF-RU0001A-01 | Compressor motor fault | Unit trip | 10 | MCC | XFHH-RU0001A-01 |  | 13 | X |  |  |  | X | X | X | X | X |  |  |  | X |  |  |  | 13
3.6 | 2 | PTC-RU0001A-13 | Compressor main motor winding U temp. high high | Unit trip | 1 | MCC | TISAHH-RU0001A-13 |  | 16 | X |  |  |  | X | X |  | X | X |  |  |  | X |  |  |  | 16
3.6 | 2 | PTC-RU0001A-14 | Compressor main motor winding V temp. high high | Unit trip | 1 | MCC | TISAHH-RU0001A-14 |  | 17 | X |  |  |  | X | X |  | X | X |  |  |  | X |  |  |  | 17
3.6 | 2 | PTC-RU0001A-15 | Compressor main motor winding W temp. high high | Unit trip | 1 | MCC | TISAHH-RU0001A-15 |  | 18 | X |  |  |  | X | X |  | X | X |  |  |  | X |  |  |  | 18
| 6 | LIT-RU0001A-01 | Chiller Liquid level high high | Unit trip | 1 | UCP | LISAHH--RU0001A-01 |  | 19 | X |  |  |  | X | X |  | X | X |  |  |  | X |  |  |  | 19
| 6 | LIT-RU0001A-01 | Chiller Liquid level low low | Unit trip | 1,2 | UCP | LISALL--RU0001A-01 |  | 20 | X |  |  |  | X | X |  | X | X |  |  |  | X |  |  |  | 20
| 2 | PIT-RU0001A-01 | Compressor Suction pressure high | Unit Alarm | 1,6 | UCP | PISAH-RU0001A-01 |  | 22 | [11 empty] | X |  |  |  |  | 22
| 2 | PIT-RU0001A-01 | Compressor Suction pressure low | Unit Alarm | 1,6 | UCP | PISAL-RU0001A-01 |  | 23 | [11 empty] | X |  |  |  |  | 23
| 3 | PIT-RU0001A-03 | Discharge pressure high | Unit Alarm | 1 | UCP | PISAH-RU0001A-03 |  | 24 | [11 empty] | X |  |  |  |  | 24
| 3 | PIT-RU0001A-03 | Discharge pressure low | Unit Alarm |  | UCP | PISAH-RU0001A-03 |  | 25 | [11 empty] | X |  |  |  |  | 25
| 2 | PDI-RU0001A-01 | Compressor Oil supply header diff. press. low | Unit Alarm | 1,4 | UCP | PDISAL-RU0001A-01 |  | 26 |  |  |  |  | X | [6 empty] | X |  |  |  |  | 26
| 2 | PDI-RU0001A-01 | Compressor Oil supply header diff. press. High | Unit Alarm | 1,4 | UCP | PDISAH-RU0001A-01 |  | 27 |  |  |  |  | X | [6 empty] | X |  |  |  |  | 27
| 3 | PDI-RU0001A-02 | Oil separator section differential pressure high | Unit Alarm | 1 | UCP | PDISAH-RU0001A-02 |  | 28 | [11 empty] | X |  |  |  |  | 28
| 4 | PDI-RU0001A-03 | Oil Filter differential pressure high | Unit Alarm | 1 | UCP | PDISAH-RU0001A-03 |  | 29 | [11 empty] | X |  |  |  |  | 29
| 3 | TIT-RU0001A-03 | Compressor Discharge temperature high | Unit Alarm | 1 | UCP | TISAH-U0001A-03 |  | 30 | [11 empty] | X |  |  |  |  | 30
| 2 | TIT-RU0001A-02 | Oil supply temperature high | Unit Alarm | 1 | UCP | TISAH-RU0001A-02 |  | 31 | [11 empty] | X |  |  |  |  | 31
| 2 | TIT-RU0001A-02 | Oil supply temperature low | Unit Alarm | 1 | UCP | TISALRU0001A-02 |  | 32 | [11 empty] | X |  |  |  |  | 32
| 3 | LS-RU0001A-01 | Oil separator level low | Unit Alarm | 1 | UCP | LISAL-RU0001A-01 |  | 33 |  |  | X | [8 empty] | X |  |  |  |  | 33
| 4 | XL-RU0001A-03 | Oil pump RU0001A-P-01 motor operation failure | Unit Alarm | 1,7 | MCC | XLH-RU0001A-03 |  | 34 |  | X | [9 empty] | X |  |  |  |  | 34
| 4 | XF-RU0001A-03 | Oil pump RU0001A-P-01 motor fault | Unit Alarm | 1,7 | MCC | XFH-RU0001A-03 |  | 35 | [11 empty] | X |  |  |  |  | 35
| 3 | XL-RU0001A-02 | Separator oil heater operation failure | Unit Alarm | 1,7 | MCC | XLH-RU0001A-02 |  | 38 | [11 empty] | X |  |  |  |  | 38
2,3,9 | 3 | XF-RU0001A-02 | Separator oil heater fault | Unit Alarm | 10 | MCC | XFH-RU0001A-02 |  | 39 | [11 empty] | X |  |  |  |  | 39
| 6 | LIT-RU0001A-01 | Chiller liquid level high | Unit Alarm | 1 | UCP | LISAH-RU0001A-01 |  | 52 | [11 empty] | X |  |  |  |  | 52
| 6 | LIT-RU0001A-01 | Chiller liquid level low | Unit Alarm | 1 | UCP | LISAL-RU0001A-01 |  | 53 | [11 empty] | X |  |  |  |  | 53
4.9 | 3 | TS-RU0001A-01B | Separator oil heater over temp. limit switch | Interlock | 1 | UCP & FIELD | TSHH-RU0001A-01B |  | 55 |  |  | X | [8 empty] | X |  |  |  |  | 55
3 | 2 | II-RU0001A-01 | Compressor High motor current hold limit | Interlock | 1 | MCC | II-RU0001A-01 |  | 58 | [9 empty] | X |  |  |  | X |  |  | 58
| 2 | II-RU0001A-01 | Compressor High motor current unload limit | Interlock | 1 | MCC | II-RU0001A-01 |  | 59 | [10 empty] | X |  |  | X |  |  | 59
| 3 | PI-RU0001A-03 | High discharge pressure hold limit | Interlock | 1 | UCP | PI-RU0001A-03 |  | 60 | [9 empty] | X |  |  |  | X |  |  | 60
| 3 | PI-RU0001A-03 | High discharge pressure unload limit | Interlock | 1 | UCP | PI-RU0001A-03 |  | 61 | [10 empty] | X |  |  | X |  |  | 61
| 2 | PI-RU0001A-01 | Low suction pressure hold limit | Interlock | 1 | UCP | PI-RU0001A-01 |  | 62 | [9 empty] | X |  |  |  | X |  |  | 62
| 2 | PI-RU0001A-01 | Low suction pressure unload limit | Interlock | 1 | UCP | PI-RU0001A-01 |  | 63 | [10 empty] | X |  |  | X |  |  | 63
| 5 | VS-RU0001A-01A | Condenser motor RU0001A-M-02 vibration high high | Interlock | 1 | UCP | VSHH-RU0001A-01A |  | 64 | [14 empty] | X |  | 64
| 5 | VS-RU0001A-01B | Condenser motor RU0001A-M-03 vibration high high | Interlock | 1 | UCP | VSHH-RU0001A-01B |  | 65 | [15 empty] | X | 65
| 5 | XL-RU0001A-04A | Condenser motor RU0001A-M-02 motor operation failure | Unit Alarm | 1,7 | MCC | XLH-RU0001A-04A |  | 66 | [11 empty] | X |  |  | X |  | 66
1 | 5 | XF-RU0001A-04A | Condenser motor RU0001A-M-02 motor fault | Unit Alarm | 10 | MCC | XFH-RU0001A-04A |  | 67 | [11 empty] | X |  |  |  | X | 67
| 5 | XL-RU0001A-04B | Condenser motor RU0001A-M-03 motor operation failure | Unit Alarm | 1,7 | MCC | XLH-RU0001A-04B |  | 68 | [11 empty] | X |  |  | X |  | 68
1 | 5 | XF-RU0001A-04B | Condenser motor RU0001A-M-03 motor fault | Unit Alarm | 10 | MCC | XFH-RU0001A-04B |  | 69 | [11 empty] | X |  |  |  | X | 69
#REF!
#REF!
Page: 2 of 2
NOTES: 1 Include any electrical faults detected by MCC. (e.g. over load, over current, low/high voltage, ground fault, open phase, reverse phase, etc.) 2 Include any electrical faults detected by MCC, and "Separator oil heater over temp. limit switch". status and "Separator oil heater box cut-out switch" status. 3 Activate by "fault signal" from MCC. Safety interlock to be created by MCC. 4 Activate "fault signal" to PLC. Alarm indication to be created commonly by "fault signal". 5 Local reset switch in the heater terminal box. 6 Cable directly connected to MCC from local equipment. 7 Caused by unit stop status and compressor stop status. 8 UCP: Unit control panel (PLC panel) / LCP: Local control panel / Local: Local equipment. MCC: Motor control centre / CCR: Central control room. 9 Source of trip must be cleared by reset , before possible reset on the HMI (UCP). 10 Only one compressor is able to operate at the same time. In case of indicated trip, stand-by compressor can be started 11 Main motor start permissive 3/2 cold/hot start-ups 12 This diagram is prepared for RU-0001A and is typical for RU-0001B with changing suffix of all tag numbers from "A" to "B". e.g. PG-RU0001B-01 | [9 empty] | Condition of activation : 1 Activate after delay timer has expired (if delay timer is applicable). 2 Activate when unit status is ”in operation”. ("In operation" = status from compressor started by start order until stop order has been received). 3 Activate when compressor motor running confirmation is activated. 4 Activate when oil pump motor running confirmation is activated. 5 Activate after 60 second from when unit status is ”in operation”. 6 Activate after 60 second from when compressor motor running confirmation is activated. 7 Activated by No running confirmation from MCC after start signal delivered, or Remaining running confirmation from MCC after stop signal delivered. 8 Activated by No running confirmation of oil pumps when compressor running. 9 Activated by both oil pump has motor fault and/or operation failure. 10 Activated by fault status signal from MCC. 11 Signal from Control room
REFRIGERATION PACKAGE
RU-0001A