## 1231 TQ Sheet
Remarks: 1- This TQ sheet shall be exchanged between PIDEC and Bidders in a native file. 2- Each column and cell shall be filled out just by concerning party means Bidders and PIDEC. 3- A telephone conversation may be held to close outstanding issues after 2 times exchanging of comments and clarification. 4- Please care that all cell to be formatted in Wrap Text setting and do not try to change column width.
EPs Contractor: |  |  | ZANJAN UREA FERTILIZER PROJECT |  |  |  | Owner:
Petrochemical Industries Design & Engineering Company (PIDEC)
TQ No.:
Project No. : 1231 |  |  | REQ No.: | 1231-DE-10-RE-REQ-330 |  | Rev.: | Project No. : 214
E.INSTRUMENT
|  | PIDEC's 1st Comment/Query |  |  | Bidder's 1st Clarification/Reply |  | PIDEC's second Comment/Query | Conclusion (2024/09/14) | Status
E.1 |  | Following Documents shall be followed by vendor for design and supplying of Control & Safety system of Package : Doc. No. : 1231-DE-00-IN-MSS-673-01 Doc. No.: 1231-DE-00-IN-MSS-602-01 (for safety loops which shall be specified based on result of HAZOP and SIL study) Doc. No. : 1231-DE-00-IN-MSS-672-02 As specification of Control & Safety system has not been cleared in Technical Offer clearly ,and there is no vendor confirmation to show that above mentioned Documents will be followed by him for design and supplying of Control & Safety system ,it is expected that any deviation to be judged and advised or confirmed by Owner. |  |  | First of all, we agreed with Owner that reference of project execution will be agreed offer and technical clarification and comments discussed and agreed. Doc. No. : 1231-DE-00-IN-MSS-672-02 is NOT available in the requisition and therefore, it is NOT considered. Comments to Doc. No. : 1231-DE-00-IN-MSS-673-01 are listed below: * Vendor equipment includes power supply, communication modules of PLC to be redundant and no further redundancy is agreed. Also, offer does NOT include any redundant I/Os same as our design in SABIC, ARAMCO, etc. Only we have ESD push bottom and remote trip signal from client ESD which are wired to separate IO cards.. * Due to the type of equipment, DELTA offer includes 10% spare on the hardware, and 20% spares of the memory. As specified in agreed offer, Instrumentation and Control will be as per MYCOM STD in Oil and Gas Area. * 2oo3 voting is not included. |  | Owner to clarify all vendor deviation points to following Project Specifications which approved by him. - Doc. No.: 1231-DE-00-IN-MSS-673-01 - Doc. No.: 1231-DE-00-IN-MSS-602-01 (for safety loops which shall be specified based on result of HAZOP and SIL study) - Doc. No.: 1231-DE-00-IN-ESS-603-01 - Vendor Deviation to Doc. No.s : 1231-DE-00-IN-MSS-673-01 & 1231-DE-00-IN-MSS-602-01 regarding redundancy of CPU & I/O cards is NOT acceptable in PIDEC Inst. Dept. point of view. Because as per Vendor clarification there is sequential STOP and SHUTDOWN sequences to protect the equipment so it seems the CPU & I/O cards to be redundant to continue sequential STOP and SHUTDOWN sequences in case of failure of one CPU or each of I/O cards. In addition ,it is not clear what redundancy of communication modules means where there is no redundancy regarding I/O cards. - Vendor Deviation to Doc. No. : 1231-DE-00-IN-MSS-673-01 & 1231-DE-00-IN-MSS-602-01 regarding spare capacity is NOT acceptable in PIDEC Inst. Dept. point of view. Because enough spare on the hardware shall be available during commissioning. And enough spare on the memory is required to be able to open several pages (alarms ,...) at the same time without any problem. - Owner to clarify Spare capacity for communication buses , power supplies based on his agreement with Vendor. - As per section SCOPE OF WORK of REQ No.: 1231-DE-10-RE-REQ-330 ,HAZOP and SIL study shall be done for Package and Vendor is responsible for the safety of package and mandatory recommendations of HAZOP/SIL studies shall be incorporated by Vendor so 2oo3 voting shall be incorporated where required based on result of SIL Study. | _Regarding Hazop and Sill study, it was agreed that The results of the HAZOP and SIL study reports will be necessary to follow for Vandor and OWNER.(WITHOUT COST EFFECT) conclusion of meeting (2024/02/17) mention in block diagram for redanduncy is applicable and shall be consider by vendor | OPEN
Comments to Doc.1231-DE-00-IN-MSS-602-01 (for safety loops which shall be specified based on result of HAZOP and SIL study) are listed below: * vendor offer includes Vendor equipment includes power supply, communication modules of PLC to be redundant and no further redundancy is agreed., but does NOT include any redundant I/Os for control nor ESD to protect the system to meet the requirements listed in this specification. * Offered equipment does NOT include a dedicated ESD system as DELTA will include special STOP and SHUTDOWN sequences to protect the equipment. This design has been used on all off-shore and on-shore equipment for safe operations. * ESD push bottom and remote trip signal from client ESD are wired to separate IO cards.
E.2 |  | Following Documents shall be followed by vendor for instruments selection/supplying and design and supplying of Control & Safety system : Doc. No. : 1231-DE-00-IN-ESS-603-01 Doc. No.: 1231-DE-10-RE-REQ-330 (section 3.18 (INSTRUMENTATION)) As specification of Control & Safety system and instruments have not been cleared in Technical Offer clearly ,and there is no vendor confirmation to show that above mentioned Documents will be followed by him for design and supplying of Control & Safety system and selection/supplying instrument ,it is expected that any deviation to be judged and advised or confirmed by Owner. |  |  | For Doc. No. : 1231-DE-00-IN-ESS-603-01, DELTA design does not allow any auto start for the 2nd compressor. The 2nd compressor shall be brought into operation manually and have both compressor load sharing. Detailed procedure will be provided during detailed engineering. Instrument located on the local control station will be hermetically sealed to meet the area class, and the JB will be Ex(ec). Locally mounted solenoid valves will be rated for Ex(de), and all transmitters will be rated for Ex(ia). Instrument taps on the compressor packages will be per manufacturer standard as shown on offered P&ID. Offered pressure gauges are 4.5". Offered Temperature gauges are 5". Due to space limitation, thermowell installation on the compressor packages are per manufacturer standard based on their common standards based many years of experience. Offered panel is per Type C. |  | - However DELTA design is not clear for us and there is no information in Vendor Technical Proposal in this regard ,it is assumed that DELTA design has been approved by Owner. Owner to confirm. - It is assumed that all Vendor deviation points to Doc. No. : 1231-DE-00-IN-ESS-603-01 have been approved by Owner. Owner to confirm. - In PIDEC Inst. Dept. point of view ,2 valve manifolds shall be used with pressure gauges, switches or transmitters. 2 valves in 1 body, 1 is the isolation valve, the other the drain/calibration valve. - In PIDEC Inst. Dept. point of view ,5-valve manifold for DP transmitters are required because of following reasons: *) Blocking a connection to the process *) Equalizing pressure between the two ports of the measuring device and to ensure that the capsule will not be over-ranged *) Bleeding the segment between the instrument and the process | _ Reagdring LOAD SHARING: two compressors will run automatically and both of them will have same load sharing to keep normal pressure at the ammonia storage. Vendor confirmed: ,2 valve manifolds shall be used with pressure gauges, switches or transmitters. 2 valves in 1 body, 1 is the isolation valve, the other the drain/calibration valve. also,5-valve manifold for DP transmitters are required because of following reasons: *) Blocking a connection to the process *) Equalizing pressure between the two ports of the measuring device and to ensure that the capsule will not be over-ranged *) Bleeding the segment between the instrument and the process | OPEN
Wire colors inside the package including remotely mounted panel are per manufacturer standard due to 1) the quantity of cable used on the system is extremely small, 2) availability in the market in small quantities. Tubing in the compressor package is manufacturer standard and may be less than 1/2". All instruments will include only main isolation valves to isolate them during service. Instrument installation and supports are per manufacturer standards.
[5 empty] | For Doc. No.: 1231-DE-10-RE-REQ-330 (section 3.18 (INSTRUMENTATION)) see below comments. * SIL Study is normally covered by a 3rd party and not vendor. * Machine Monitoring Vibration equipments are not offered due to the size of the equipment and not required. * Due to the type of equipment, Vendor offer includes 10% spare on the hardware, and 20% spares of the memory. * 2oo3 voting is not included. * Vendor equipment includes power supply, communication modules of PLC to be redundant and no further redundancy is agreed. |  | Please refer to PIDEC's second Comment/Query to item E.1. |  | OPEN
|  | It is expected that items E.3 ~ E.39 to be followed by Vendor so in case of any deviation ,it should be judged and advised or confirmed by Owner. |  |  | Refer to below reply.
E.3 |  | Original software and operating systems with all required licenses (Soft key or Hard key) shall be provided for Engineering Laptop and A copy of all original software with their licenses and also a copy of database of package software on compact disk (CD or DVD) shall be deliver to owner separately. |  |  | Operation software will be provided, configuration software is property of Vendor. DELL/ Lenovo Brand Cori5 laptop will be provided/ |  | It is NOT acceptable in PIDEC point of view. Installation of original engineering/configuration software with their licenses on Engineering Laptop and delivery of copy of database of package software on compact disk (CD or DVD) to Owner are mandatory otherwise the vendor shall be present for any modification in future. It addition it is not clear where Operation software will be installed by Vendor. Any PC station (desktop computer) was not found in Vendor offer. | vendor confirmed that provid and. Install of original engineering/configuration software with their licenses on Engineering Laptop be able to upload and download program without change the program | OPEN
E.4 |  | Since the control cabinets will be installed in control room ,minimum IP42 is required for the cabinets. |  |  | Confirmed |  |  |  | CLOSED
E.5 |  | Field instruments shall be smart instruments with 4~20 mA signal and HART protocol. |  |  | Confirmed |  |  |  | CLOSED
E.6 |  | Electronic transmitters in hazardous area shall be basically intrinsic safe. Solenoid valves shall be Exia. |  |  | Confirmed for transmitters, however, solenoid valves, hand switches, push button, and pilot lights are Ex(d) |  | Explosion proof cable glands shall be used. | _Confirmed by Vnedor | OPEN
E.7 |  | All limit switches for automatic valves shall be proximity (NUMOR) type and intrinsically safe. |  |  | Housing for compressor slide valve assembly that includes limit switches and potentiometers is indeed Ex(ia) but requires barriers *current convertor) located inside the panel. |  | Type of limit switches for automatic valves are NOT clear. Please clarify. | Clrified by vendor and confirmed | OPEN
E.8 |  | Solenoid valves shall be IS with 24 VDC voltage rating. The material of body and trim to be SS 316. Coil housing material to be metallic not plastic. It should be noted that : - The distance between PU-5001 (Refrigeration Package) in Field and Package PLC and its marshalling cabinet in auxiliary room is approximately 260 meters. - The multi cable type which will be used for solenoid valves is 10x(2x1.5)+SCR. |  |  | Confirmed |  | The multi cable type which will be used for solenoid valves is 10x(2x2.5)+SCR. | Clrified by vendor and confirmed | CLOSED
E.9 |  | All transmitters shall be provided with integral digital indicators. |  |  | Confirmed |  |  |  | CLOSED
E.10 |  | Isolating valves shall be provided for all instruments. Two valve manifold for pressure switches and gauges and 5-valve manifold for DP transmitters shall be considered. |  |  | All transmitter will be located locally and only route valves will be used for isolation and mani fold is not required. |  | Please refer to PIDEC's second Comment/Query to item E.2. |  | OPEN
E.11 |  | All cable entries shall be M20X1.5 with explosion-proof cable glands. It shall be suitable for armored cable. |  |  | Confirmed |  |  |  | CLOSED
E.12 |  | The instrumentation shall be rated to withstand the environmental conditions specified in the engineering standard specification for ambient and site condition. |  |  | Confirmed |  |  |  | CLOSED
E.13 |  | All instrument/automatic valves wetted parts and process/air tubing materials shall be S.S. 316 as minimum, other materials as per process conditions. |  |  | Tubings will be SS 316 |  | Since selecting proper material base on process condition is Vendor responsibility it is assumed that SS 316 is suitable. |  | CLOSED
E.14 |  | Where ever temperature shall be transmitted to the package PLC, temperature transmitter shall be provided by vendor. Direct connection of temperature element to PLC is not acceptable. |  |  | Confirmed with the following clarifications: * Winding RTD are wired directly to MCC(if MV motor) * Compressor bearing RTDs are not required and agreed. * Motor bearing RTDs are not provided since the motor is ant-friction ball bearing |  |  | Refer to meeting conclusion (2024-09-14) it was agreed that vendor to consider RTD for each beaing of motor. | CLOSED
E.15 |  | Emergency shutdown sensors shall not be common with those of control loops. |  |  | Confirmed as for fail safe system, ESD button is a hard wire and normally wired to kill all outputs from PLC. |  | Vendor reply is NOT clear ,Owner to clarify based on his agreement with Vendor. |  | OPEN
E.16 |  | All field instruments shall be factory calibrated with calibration certificate. |  |  | Confirmed |  |  |  | CLOSED
E.17 |  | In addition to isolation valve, dedicated manifold shall be considered and provided by vendor in each instrument hook up (for pressure & diff. pressure instruments). |  |  | All transmitter will be located locally and only route valves will be used for isolation and mani fold is not required. |  | Please refer to PIDEC's second Comment/Query to item E.2. |  | OPEN
E.18 |  | For off-skid loose and skid mounted instruments, all related Single Cables (40 meter for each item), Cable Glands, open conduits, pipe, tube (in SS316), fittings (in SS316), isolation and drain valves, manifolds, junction boxes, cable trays, instrument support, etc. shall be supplied by vendor based on Process & air Instrument Hook-ups and Instrument Field layout which shall be supplied by him. |  |  | Confirmed and all installation drawing will be shared during design review |  |  |  | CLOSED
E.19 |  | Skid & off-skid loose instruments and JB locations and cable routing shall be shown on Instrument Field layout. |  |  | Vendor confirms the following in the 3D model: * Cable trays routing * Instrument hookup with tube routing * Instrument location |  | In addition to 3D Model following Documents shall be submitted by Vendor. - Instrument Field layout - Instrument Process Hook Up’s | 3D modeling with Autocad 3D (be able to convert STP format) - that can be implemented in whole plant modeling- shall be provided by vendor | OPEN
E.20 |  | All panels, enclosures and junction boxes shall be explosion protected according to their area classification. All field mounted instruments, enclosures and junction boxes shall be protected to IP-65. |  |  | Confirmed for skid mounted instruments and junction boxes |  | It is expected that mentioned requirement to be followed by Vendor for off-skid loose instruments as well. Owner to clarify based on his agreement with Vendor. | vendor confirmed that All panels, enclosures and junction boxes explosion protected according to their area classification. All field mounted instruments, enclosures and junction boxes shall be protected to IP-65. | OPEN
E.21 |  | Terminals No. in Package PLC cabinets shall be mirror of terminals in junction boxes/interposing cabinet. |  |  | Confirmed |  |  |  | CLOSED
E.22 |  | All plant cables shall be fire retardant. |  |  | Confirmed per IEC 331 and IEC 332 |  |  |  | CLOSED
E.23 |  | The available power supply in the control room is 110 V AC, 50 Hz UPS (redundant feeders in control room). Any requirement to another level of voltage , are in vendor scope of supply. Any distribution for 110VAC/UPS inside the package battery limit, are in vendor scope of supply as well. Also one 230VAC, non UPS will be made available by purchaser for Internal lamps and socket outlets in PLC cabinets of package. |  |  | Confirmed and noted |  |  |  | CLOSED
E.24 |  | Page 6 of 16 of Doc. No.:1231-DE-00-IN-SKT-007 shall be followed by vendor for Instrument/Electrical Connection Details as a typical sketch for signals which are applicable for vendor's electrical motors. Signals from/to MCC’s shall be considered as non-IS and hardwire type. All digital inputs/outputs from/to MCC shall be relay type (relays must be in vendor cabinet and shall be powered from vendor cabinet (output contact from these relays shall be wet and powered by 24Vdc inside PLC)). |  |  | Noted. |  | It is expected that mentioned requirement to be followed by Vendor. Owner to clarify based on his agreement with Vendor. |  | OPEN
E.25 |  | TAG No. of each terminal strip in Package PLC cabinets shall be same as MULTICORES No. which will be specified by purchaser. |  |  | Confirmed |  |  |  | CLOSED
E.26 |  | IS and NIS signals shall be separated inside panels. (Two rout cables shall be considered). As per IEC-60332-1/BS-5308, IS cables shall be blue and NIS cables shall be gray. |  |  | Confirmed |  |  |  | CLOSED
E.27 |  | Separate IE/PE earth bar shall be considered inside the panels. |  |  | Confirmed |  |  |  | CLOSED
E.28 |  | Redundant DI & DO signals shall be foreseen by vendor for communication with plant hardwire console (Supplied by others). HS-50301 (Emergency Stop Signal; Trip PU-5001)(NIS,REDUNDANT,PASSIVE,24 VDC / POTENTIAL FREE CONTACT) HL-50301 (Common shutdown alarm from package PLC (UCP) to Plant HWC)(NIS,REDUNDANT,PASSIVE,24 VDC (CONSUMER LOAD)) |  |  | Vendor does offer redundant DI & DO for the following reasons: * Vendor equipment includes power supply, communication modules of PLC to be redundant and no further redundancy is agreed.s, but does NOT include any redundant I/Os. * Offered equipment does NOT include a dedicated ESD system as Vendor will include sequential STOP and SHUTDOWN sequences to protect the equipment. This design has been used on all off-shore and on-shore equipment for safe operations. * ESD push bottom and remote trip signal from client ESD are wired to separate IO cards.. * System will detect a bad PV anytime trip devices are failing. All hardwired signal for ESD will be wired to two different DI card to assure redundancy. DELTA offer requires all signal in dry state. |  | - Please refer to PIDEC's second Comment/Query to item E.1. - Refer to Vendor explanation as there is sequential STOP and SHUTDOWN sequences to protect the equipment ,it is assumed that by activation of HS-50301 sequential STOP/SHUTDOWN sequences will be started. To be clarified. - Again it should be noted that : HS-50301 on Plant-Hard wire console (supplied by others) has been considered and related signal will be sent to Package PLC (supplied by Vendor). HL-50301 (Common shutdown alarm (Lamp)) has been considered on Plant-Hard wire console (supplied by others) to indicate activation of Trip signal. Trip signal should be sent from Package PLC (supplied by Vendor) to Plant-Hard wire console (supplied by others) and Signal type to be 24 VDC (CONSUMER LOAD). Digital output modules shall energize output relays by 24 V DC. | _Noted and Confiremd. _Output Relay will be supplied by Vendor. _vendor confirmed that indication TRIP signal sent to Plant-Hard wire console From interposing relay . | OPEN
E.29 |  | The required shut-down, start-up and inter-lock diagrams based on IEC 61131 shall be provided and implemented in packages PLC’s by Vendor. |  |  | Vendor standard documents will be provided for the following: * Set point List * C&E * IO List * ¦Control Narrative + Startup, Stop, and ESD Sequences. |  | It is assumed that sequential function charts to be according to IEC-60848 (as per Doc. No.: 1231-DE-00-IN-MSS-602-01). To be clarified. All Documents listed in part "TECHNICAL DOCUMENTS/INSTRUMENTATION" of RFD Form shall be submitted by VENDOR. Although Vendor VPIS has been commented in this regard any reply to VPIS has not been received. | _Cause and Effect and interlock diagram will be add to document list. Proposed VPIS + C&E + Interlock Diagram. | OPEN
E.30 |  | The system logic shall be ‘fail safe’. All instruments shall be considered for fail to safe action upon loss of instrument air or electrical power. The input contacts to alarm, interlock and emergency shutdown system shall be close (make contact) during normal operation and open on alarm or trip. The solenoids shall be energized during normal operation and de-energized to trip. |  |  | Confirmed |  |  |  | CLOSED
E.31 |  | The PLC’s shall be provided with all required system software including application/utility programs, engineering/configuration tools, self-checking and self diagnostic fault detection capabilities. |  |  | Operation software will be provided, configuration software is property of Vendor. DELL/ Lenovo Brand Cori5 laptop will be provided/ |  | It is not clear where system software including application/utility programs, self-checking and self diagnostic fault detection capabilities will be installed based on Vendor agreement with Owner. |  | OPEN
E.32 |  | Vendor shall supply any required software/hardware for configuration of the PLC. The required soft-wares shall be installed on the laptop. The original software/dungle shall be included. |  |  | Operation software will be provided, configuration software is property of Vendor. DELL/ Lenovo Brand Cori5 laptop will be provided/ |  | Please refer to PIDEC's second Comment/Query to item E.3. |  | OPEN
E.33 |  | All instrument items which are in vendor scope of supply and will be supplied as loose items by vendor shall be packed in separate box and marked properly "for instrumentation" during packing and shipment stage. |  |  | Confirmed |  |  |  | CLOSED
E.34 |  | The HAZOP and SIL study for package PIDs (vendor scope of work and supply) shall be performed by Vendor through third party. The Vendor quotation shall include all costs of performing HAZOP and SIL Studies for package PIDs including meetings, moderator, documentation, etc. The study results including HAZOP reports, HAZOP action close out sheets, SIL assessment and verification reports shall be submitted by vendor or study moderator as package vendor documents. The HAZOP study shall be performed according to IEC 61882 requirements. The SIL assessment/verification shall be performed according to IEC 61508 and IEC 61511 requirements. Since the Vendor is responsible for safety of package, all mandatory recommendations of HAZOP/SIL studies shall be incorporated without additional cost. |  |  | HAZOP and SIL studies are normally covered by contractor and NOT vendors. We will participate in client meeting with third party |  | As refer to section SCOPE OF WORK of REQ No.: 1231-DE-10-RE-REQ-330 ,HAZOP and SIL study shall be considered by Vendor as Main Quotation ,any deviation in this regard shall be confirmed by Owner. Owner to confirm. |  | OPEN
E.35 |  | All the system hardware (including monitoring, control, protection, communications, communication with DCS, etc.) complete with all software (including application software) installed and loaded on the corresponding hardware, are subject to Factory Acceptance Test (FAT). FAT procedure shall be prepared by Vendor, approved by Owner and used as the guideline for performing FAT. Owner reserves the right to modify Vendor’s standard procedure. |  |  | Confirmed |  |  |  | CLOSED
E.36 |  | When Factory Acceptance Test (FAT) is over, the following features shall be available for future expansion: • a minimum of 20% installed spare breakers/fuses, • a minimum of 20% installed spare cores/pairs/triples terminals, • a minimum of 20% installed input/output spare points, • a minimum of 20% free space in cabinets, • 50% spare capacity for communication buses • 50% spare capacity for memory • 30% spare capacity for power supplies • 40% spare capacity for process controller unit |  |  | Refer to 1st item reply, these high requirement are not needed and nor agreed with Owner |  | Please refer to PIDEC's second Comment/Query to item E.1. |  | OPEN
E.37 |  | Commissioning and two years spare parts for instruments shall be quoted. Two years spare parts shall be according to Att. No. : 4 of Doc. No.: 1231-DE-10-RE-REQ-330 (Specific List of Spare Parts). |  |  | As per list provided by Owner |  |  |  | CLOSED
E.38 |  | Vendor's proposals shall cover the training according to section 12.6 of Doc. No.: 1231-DE-00-IN-MSS-673 (as an option). |  |  | As per agreement with Owner |  |  |  | CLOSED
E.39 |  | As most of Inst. Dept. technical documents were not found in submitted VPIS ,VPIS should be modified according to comments marked in green color. Vendor documentation shall be in PROJECT format. |  |  | Please find our replies |  | Owner is kindly requested to review PIDEC Inst. Dept. reply (in red color) to attached Excel file "Inst. Dept. reply to VPIS (Commented by Instrument Dept.)-Replied 22 July" and advice regarding documentation based on your agreement with Vendor. |  | OPEN