## Cover
Toase-ehe Park Sanati Gohar Ofogh Petrochemical Co. CONCEPTUAL, BASIC and DETAIL DESIGN ENGINEERING OF STYRENE PARK OFFSITE
Document Title: Instrument Data Sheet for Basket Filter
|  | Document No. : EI027-ENR-VD-IN-DSH-003 |  | Rev.: R1 | Page 1 of 3
STYRENE PARK OFFSITE Document Title: Instrument Data Sheet for Basket Filter
R1 | 2024-12-06 | Final Issue | A.Mohamadhoseini | E.Malek | H.Keshmiri
R0 | 17/04/2024 | Issued for Comment | A.Mohamadhoseini | E.Malek | H.Keshmiri
Rev. | Issued Date | DESCRIPTION | PREPARED | CHECKED | APPROVED

## Index
Toase-ehe Park Sanati Gohar Ofogh Petrochemical Co. CONCEPTUAL, BASIC and DETAIL DESIGN ENGINEERING OF STYRENE PARK OFFSITE
Document Title: Instrument Data Sheet for Basket Filter
|  |  |  | Document No. : EI027-ENR-VD-IN-DSH-003 | [6 empty] | Rev.: R1 |  | Page 2 of 3
Page | Revisions | [6 empty] | Page | Revisions
| R0 | R1 | R2 | R3 | R4 | R5 | R6 |  | R0 | R1 | R2 | R3 | R4 | R5 | R6
1 | X | X | [5 empty] | 41
2 | X | X | [5 empty] | 42
3 | X | X | [5 empty] | 43
4 | [7 empty] | 44
5 | [7 empty] | 45
6 | [7 empty] | 46
7 | [7 empty] | 47
8 | [7 empty] | 48
9 | [7 empty] | 49
10 | [7 empty] | 50
11 | [7 empty] | 51
12 | [7 empty] | 52
13 | [7 empty] | 53
14 | [7 empty] | 54
15 | [7 empty] | 55
16 | [7 empty] | 56
17 | [7 empty] | 57
18 | [7 empty] | 58
19 | [7 empty] | 59
20 | [7 empty] | 60
21 | [7 empty] | 61
22 | [7 empty] | 62
23 | [7 empty] | 63
24 | [7 empty] | 64
25 | [7 empty] | 65
26 | [7 empty] | 66
27 | [7 empty] | 67
28 | [7 empty] | 68
29 | [7 empty] | 69
30 | [7 empty] | 70
31 | [7 empty] | 71
32 | [7 empty] | 72
33 | [7 empty] | 73
34 | [7 empty] | 74
35 | [7 empty] | 75
36 | [7 empty] | 76
37 | [7 empty] | 77
38 | [7 empty] | 78
39 | [7 empty] | 79
40 | [7 empty] | 80

## PDIT
Toase-ehe Park Sanati Gohar Ofogh Petrochemical Co. CONCEPTUAL, BASIC and DETAIL DESIGN ENGINEERING OF STYRENE PARK OFFSITE
Document Title: Instrument Data Sheet for Basket Filter
|  |  | Document No. : EI027-ENR-VD-IN-DSH-003 | [7 empty] | Rev.: R1 | Page 3 of 3
DATA SHEET FOR DIFFERENTIAL PRESSURE TRANSMITTER
GENERAL | 1 | Item Number | Tag Number |  | QTY. |  | 1 | See Table A |  |  |  |  | 2
| 2 | Service |  |  |  |  | See Table A
| 3 | P&ID No. |  |  |  |  | EI027-HRC-VD-PR-PID-003-R3
| 4 | Line/Equipment No. |  |  |  |  | See table A
PROCESS CONDITIONS | 5 | Fluid |  | Phase |  |  | Air+Styrene (3.5 g/Nm3) |  |  |  | Vapor
| 6 | Oper. Pressure | Min. | Nor. | Max. | Unit | -0.08 |  | 0.02 |  | 0.02 |  | barg
| 7 | Oper. Diff. Press. |  | Min. | Max. | Unit | See table A |  |  | See table A |  |  | bar
| 8 | Oper. Temp. |  |  |  | Unit | 15 | [5 empty] | C
| 9 | Design Pressure |  |  |  | Unit | 3.5 | [5 empty] | barg
| 10 | Design Temp. |  |  |  | Unit | 85 | [5 empty] | C
| 11 | Operating Viscosity |  |  |  | Unit | 0.02 | [5 empty] | cP
| 12 | Pulsation |  |  |  |  | No
| 13 | Corrosive Service |  | Super Heat |  |  | Yes |  |  |  | No
| 14 | Toxic Service |  | NACE Requirement |  |  | Yes |  |  |  | No
TRANSMITTER | 15 | Instrument Type |  | Model |  |  | DIFFERENTIAL PRESSURE TRANSMITTER |  |  |  | V.T.A
| 16 | Instrument Range |  | Calibration Range |  | Unit | –621.60 to 621.60 mbar (V.T.C) |  |  |  | 0 - (0.2) |  | barg
| 17 | Zero Adjustment |  | Span Adjustment |  |  | Yes |  |  |  | Yes
| 18 | Integrated Local Indicators |  |  |  |  | LCD Required
| 19 | Power Supply |  | Power Consumption |  |  | 24 vDC |  |  |  | V.T.A
| 20 | Output Signal |  | Electrical Connection |  |  | 4-20 mA |  |  |  | M20*1.5
| 21 | Housing Material |  |  |  |  | Die-Cast Aluminum
| 22 | Ex Certificate |  |  |  |  | Ex'd' IIB T3
| 23 | Ingress Protection |  |  |  |  | IP 65
SENSING & BODY | 24 | Element Type |  | Element Material |  |  | Diaphragm Type |  |  |  | S.S 316
| 25 | Body Material |  |  |  |  | S.S 316
| 26 | Instrument Connection |  |  |  |  | 1/2" NPTM
| 27 | Accuracy |  |  |  |  | ±0.15 % of Calibration span
DIAPHRAGM SEAL | 28 | Model Number |  |  |  |  | N/A
| 29 | Type |  |  |  |  | N/A
| 30 | Process Connection |  |  |  |  | N/A
| 31 | Connection Material |  | Connection Rating |  |  | N/A
| 32 | Extended Length |  |  |  |  | N/A
| 33 | Diaphragm Material |  |  |  |  | N/A
| 34 | Bottom Housing Material |  |  |  |  | N/A
| 35 | Fill Fluid |  |  |  |  | N/A
| 36 | Capillary Length |  |  |  |  | N/A
| 37 | Capillary Bleeder |  |  |  |  | N/A
| 38 | Capillary Material |  |  |  |  | N/A
| 39 | Flushing Connection |  |  |  |  | N/A
| 40 | Top Housing Material |  |  |  |  | N/A
OPTIONS | 41 | Siphon |  | Type / Material |  |  | N/A |  |  |  | N/A
| 42 | Snubber |  | Material |  |  | N/A |  |  |  | N/A
| 43 | Over range Protector |  | Material |  |  | N/A |  |  |  | N/A
| 44 | Oil Filled |  |  |  |  | N/A |  |  |  | N/A
MANIFOLD | 45 | Valve Type |  | Model |  |  | 5-Way Valve |  |  |  | V.T.A
| 46 | Body Material |  | Trim Material |  |  | S.S 316 |  |  |  | S.S 316
| 47 | Process Connection/Instrument Connection |  |  |  |  | 1/2" NPTM
| 48 | Vent/Drain size/ Valve Rating |  |  |  |  | 1/4" NPTM/3000#
| 49 | Packing Material |  |  |  |  | PTFE
PURCHASE | 51 | Manufacturer
| 52 | Model
53
Notes:
Table A
|  |  | item | Tag No. | Service |  | Line No./Equip. No |  | Oper. Diff. Press. (Bar) |  | Remark
[9 empty] | min. | max.
|  |  | 1 | PDIT-0003 | Basket Filter |  | PK-0001-A |  | 0.06 | 0.1
|  |  | 2 | PDIT-0004 | Basket Filter |  | PK-0001-B |  | 0.06 | 0.1
R1
R1