| Main Motor Data Sheet and Curve |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| PURCHASER'S COMMENT/APPROVAL STATUS |  |  |  |  |  |  | Purchaser: NARGAN |
| 1 | AP: Approved (Released for Manufacturing) |  |  |  |  |  |  |
| 2 | AN: Approved With Minor Comments (Fabrication may Proceed) |  |  |  |  |  | Requisition No.: DPIC98-12-001-000-ME-MR-4150-0001-D1 |
| 3 | NF: Approved With Comments (Fabrication not Proceed) |  |  |  |  |  |  |
| 4 | RJ: Rejected |  |  |  |  |  | Item No. (Tag No.): PK-6101 |
| 5 | NR: Not be Returned |  |  |  |  |  |  |
| Date: Signature: |  |  |  |  |  |  | Vendor Doc. No.: DPIC9812-000-VD-1002-ME-DS-0042 |
| D2 |  | 20-July-22 | IFA | P.Sh | E.S | N.S |  |
| D1 |  | 21-Feb-22 | IFA | NA.PR | M.M | A.V |  |
| D0 |  | 23-Jan-22 | IFA | NA.PR | M.M | A.V |  |
| REV. |  | DATE ISSUE | Purpose of Issue | PREPARED | CHECKED | APPROVED |  |

| Page | Rev-D0 | Rev-D1 | Rev-D2 | Rev-D3 | Rev-D4 |  | Page | Rev-D0 | Rev-D1 | Rev-D2 | Rev-D3 | Rev-D4 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | x | x | x |  |  |  | 36 |  |  |  |  |  |  |
| 2 | x | x | x |  |  |  | 37 |  |  |  |  |  |  |
| 3 | x | x | x |  |  |  | 38 |  |  |  |  |  |  |
| 4 | x | x | x |  |  |  | 39 |  |  |  |  |  |  |
| 5 | x | x | x |  |  |  | 40 |  |  |  |  |  |  |
| 6 | x | x | x |  |  |  | 41 |  |  |  |  |  |  |
| 7 | x | x | x |  |  |  | 42 |  |  |  |  |  |  |
| 8 | x | x | x |  |  |  | 43 |  |  |  |  |  |  |
| 9 |  |  |  |  |  |  | 44 |  |  |  |  |  |  |
| 10 |  |  |  |  |  |  | 45 |  |  |  |  |  |  |
| 11 |  |  |  |  |  |  | 46 |  |  |  |  |  |  |
| 12 |  |  |  |  |  |  | 47 |  |  |  |  |  |  |
| 13 |  |  |  |  |  |  | 48 |  |  |  |  |  |  |
| 14 |  |  |  |  |  |  | 49 |  |  |  |  |  |  |
| 15 |  |  |  |  |  |  | 50 |  |  |  |  |  |  |
| 16 |  |  |  |  |  |  | 51 |  |  |  |  |  |  |
| 17 |  |  |  |  |  |  | 52 |  |  |  |  |  |  |
| 18 |  |  |  |  |  |  | 53 |  |  |  |  |  |  |
| 19 |  |  |  |  |  |  | 54 |  |  |  |  |  |  |
| 20 |  |  |  |  |  |  | 55 |  |  |  |  |  |  |
| 21 |  |  |  |  |  |  | 56 |  |  |  |  |  |  |
| 22 |  |  |  |  |  |  | 57 |  |  |  |  |  |  |
| 23 |  |  |  |  |  |  | 58 |  |  |  |  |  |  |
| 24 |  |  |  |  |  |  | 59 |  |  |  |  |  |  |
| 25 |  |  |  |  |  |  | 60 |  |  |  |  |  |  |
| 26 |  |  |  |  |  |  | 61 |  |  |  |  |  |  |
| 27 |  |  |  |  |  |  | 62 |  |  |  |  |  |  |
| 28 |  |  |  |  |  |  | 63 |  |  |  |  |  |  |
| 29 |  |  |  |  |  |  | 64 |  |  |  |  |  |  |
| 30 |  |  |  |  |  |  | 65 |  |  |  |  |  |  |
| 31 |  |  |  |  |  |  | 66 |  |  |  |  |  |  |
| 32 |  |  |  |  |  |  | 67 |  |  |  |  |  |  |
| 33 |  |  |  |  |  |  | 68 |  |  |  |  |  |  |
| 34 |  |  |  |  |  |  | 69 |  |  |  |  |  |  |
| 35 |  |  |  |  |  |  | 70 |  |  |  |  |  |  |

| MV MOTOR Data Sheet FOR ZONE 2 + H2 PRESENCE |  |  |
| --- | --- | --- |
| APPLICABLE TO: [ ] PROPOSAL [X] PURCHASE [ ] AS BUILT |  |  |
| A: MOTOR MAIN DATA |  |  |
| 1 | ITEM : CM-6101A & CM-6101B | QUANTITY: 2 |
| 2 | GENERAL FEATURES ACCORDING TO : IEC Standards - IPS Standards - ISO Standards DPC-EL-SPC-0020- Medium Voltage Motor Specification |  |
| 3 | MOTOR TESTING ACCORDING TO: IEC Standards - IPS Standards |  |
| 4 | RATED POWER : 1340 kW | NUMBER OF POLES : 2 N° |
| 5 | RATED VOLTAGE : 6 kV ± 5% | NUMBER OF PHASES : 3 N° |
| 6 | RATED FREQUENCY : 50 Hz ± 2% | POWER FACTOR REQUIRED: cosφ≥ 0.85 |
| 7 | FRAME SIZE: 450 | CONNECTION TYPE: [ X ]STAR [ ] DELTA [ ] WYE |
| 8 | TYPE OF DUTY: CONTINOUS (S1) [ ] FOR EXTRUDER [X] OTHERS: Screw Compressor |  |
| 9 | DIRECTION OF ROTATION (seen from shaft end): [ X ] CLOCKWISE [ ] COUNTER-CLOCKWISE [ ] BOTH |  |
| 10 | NAME PLATE INCLUDES FOLLOWING ITEMS: [ X ] 1.IP classification 2.Bearing and lubrication references 3.Purchase order number and year of manufacture 4.Weight 5.Type of protection (for safe use in hazardous areas) 6.Apparatus group 7.Temperature group 8.Temperature classification 9.Certification mark and certification number 10.Rated voltage, current, PF and efficiency | FAULT LEVEL: # ………………………………………………… |
| 11 | COOLING:[ ] WATER COOLED TYPE: IC611 [ X ] FAN COOLED, TOTALLY ENCLOSED TYPE:………….. |  |
| 12 | MOUNTING ARRANGEMENT: (Note 2) |  |
| 13 | [ ] CODE 1 [ X ] IM B3 [ ] IM B5 [ ] IM B7 |  |
| 14 | [ ] CODE 2 SPECIFY: ………………………………………………………………………………. |  |
| 15 | ENCLOSURE: (Note 3) | MANUFACTURER: HELMKE |
| 16 | [ ] IP44 [ X ] IP55 (for MOTOR) [ X ] IP55 (for T.B.) | MANUFACTURER'S CODE: NDKK450-02-G |
| 17 | [ ] OTHERS: SPECIFY | ORDER N°: |
| 18 | [ ] MATERIAL TYPE: Welded steel | PROJECT LOCATION: DEHDASHT (IRAN) |
| B: DATA OF DRIVEN MACHINE |  |  |
| 1 | TYPE OF MACHINE: Screw Compressor | SERVICE DESCRIPTION: Propylene Refrigeration Package |
| 2 | ITEM: C-PK-6101-1A/B | MOMENT OF INERTIA AT MOTOR AXIS: 16,0 kg*m² |
| 3 | DATA SHEET: DPIC9812-000-VD-1002-ME-DS-0041 | STARTING RESISTING TORQUE: ~ 10 % |
| 4 | ORDER AND SUPPLIER: KASRAVAND | MAXIMUM RESISTING TORQUE: 960 Nm |
| 5 | INPUT POWER: 1206 kW (input electrical power) | SPEED: 2950 rpm |
| 6 | MECHANICAL REQUIRED POWER: 1160 kW | CUOUPLING TYPE: [ ] STIFF [X] FLEXIBLE [ ] BELT [ ]OTHER |
| C: PROTECTION FOR HAZARDOUS LOCATIONS DUE TO GAS AND VAPOURS (Note 3) |  |  |
| 1 | ZONE:[ ] NON HAZARDOUS [ ] ZONE 0 [ ] ZONE 1 [ X ] ZONE 2 |  |
| 2 | EQUIPMENT CATEGORY: [ ] 1G [ ] 2G [X] 3G |  |
| 3 | GAS & VAPOURS GROUP: [ ] IIA [ ] IIB + HZ [X] IIC |  |
| 4 | TEMPERATURE CLASS: [X] T3 [ ] T4 [ ] T5 [ ] T6 |  |
| 5 | TYPE OF PROTECTION:[ ] Ex-d [ ] Ex-de [X] Ex-ec [ ] Ex-p [ ] Ex-n |  |

| D: PROTECTION FOR HAZARDOUS LOCATIONS DUE TO DUSTS (Note 3) |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | ZONE: [ ] ZONE 20 [ ] ZONE 21 [ ] ZONE 22 |  |  |  |  |  |  |  |  |  |  |
| 2 | TYPE OF DUSTS: [ ] CONDUCTIVE [ ] NON CONDUCTIVE REFER TO :TM 751.1 |  |  |  |  |  |  |  |  |  |  |
| 3 | EQUIPMENT CATEGORY: [ ] 1D [ ] 2D [ ] 3D |  |  |  |  |  |  |  |  |  |  |
| 4 | TYPE OF PROTECTION: [ ] Ex-tD [ ] Ex-pD SURFACE TEMPERATURE (Tmax.): ……...°C |  |  |  |  |  |  |  |  |  |  |
| E: NETWORK CHARACTERISTICS |  |  |  |  |  |  |  |  |  |  |  |
| 1 | SHORT CIRCUIT CURRENT, R.M.S : 25 /1 kA / s |  |  |  | SHORT CIRCUIT CURRENT, PEAK: kA |  |  |  |  |  |  |
| 2 | NEUTRAL STATUS [ ] SOLIDLY EARTHED [ X ] EARTHED THROUGH RESISTOR [ ] INSULATED |  |  |  |  |  |  |  |  |  |  |
| F: MOTOR OPERATING CHARACTERISTICS AND PARAMETERS |  |  |  |  |  |  |  |  |  |  |  |
| 1 | RATED SPEED: 2984 RPM |  |  |  | STARTING TORQUE: (Note 22) 0,6 Nm |  |  |  |  |  |  |
| 2 | CONTINOUS VARIABLE SPEED FROM/TO N/A |  |  |  | BREAK-DOWN TORQUE: 2.50 Nm |  |  |  |  |  |  |
| 3 | FULL LOAD AMPERE: 150 A |  |  |  | SLIP AT FULL LOAD: |  |  |  |  |  |  |
| 4 | FULL LOAD TORQUE: 4289 Nm |  |  |  | PULL-UP TORQUE (AT RATED VOLTAGE): 0.59 % |  |  |  |  |  |  |
| 5 | STARTING CURRENT: (Note 4) 5,5 x FLA (550% In) |  |  |  | OPEN CIRCUIT TIME CONSTANT: S |  |  |  |  |  |  |
| 6 | STARTING TIME AT FULL LOAD: 3 S |  |  |  | SYSTEM EARTHING: Grounded trough Resistance |  |  |  |  |  |  |
| 7 | NO LOAD CURRENT: A |  |  |  | Min. GROUNDING CONDUCTOR: |  |  |  |  |  |  |
| 8 | SERVICE FACTOR: (Note 5) 1 |  |  |  | THERMAL TIME CONSTANT ………………… |  |  |  |  |  |  |
| 9 | NOISE PRESSURE LEVEL AT 1 m: 78+3 dB(A) ≤ 82 |  |  |  | COOLING: 176 min |  |  |  |  |  |  |
| 10 | NUMBER OF STARTS PER HOUR:LOAD % 100 80 |  |  |  | HEATING: min |  |  |  |  |  |  |
| 11 | COLD: 3 |  |  |  |  |  |  |  |  |  |  |
| 12 | HOT: 2 |  |  |  | CURVES REQUIRED BASED ON MOTOR SATURATION AT RATED V. |  |  |  |  |  |  |
| 13 | INERTIA CONSTANT (H): 0.52 |  |  |  | [X] SPEED VS TORQUE(ALSO AT 80% RATED VOLTAGE) |  |  |  |  |  |  |
| 14 | MOMENT OF INERTIA: 16,0 kg*m² |  |  |  | [ ] SPEED VS POWER FACTOR |  |  |  |  |  |  |
| 15 | IMPEDANCE/PHASE: OHM Ucc% |  |  |  | [X] SPEED VS CURRENT (ALSO AT 80% RATED VOLTAGE) |  |  |  |  |  |  |
| 16 | ROTOR CLASS |  |  |  | TIME-CURRENT HEATING CURVE: YES |  |  |  |  |  |  |
| 17 | AC STATOR RESISTANCE: ……….OHM AT………..…°C |  |  |  |  |  |  |  |  |  |  |
| 18 | REACTANCE AND EQUIVALENT CIRCUIT PARAMETERS : |  |  |  | DIMENSIONS: |  |  |  |  |  |  |
| 19 | SUB TRANSIENT (X"d): |  |  |  | LENGTH: 3482 mm |  |  |  |  |  |  |
| 20 | TRANSIENT (X'd): |  |  |  | WIDTH: 1743 mm |  |  |  |  |  |  |
| 21 | SYNCHRONOUS (Xd): |  |  |  | DEPTH: 1848 mm |  |  |  |  |  |  |
| 22 | STATOR LEACKEGE REACTANCE X1 : FOR MOTOR EQUIVALENT CIRCUIT PARAMETERS PLEASE REFER TO ATTACHMENTS |  |  |  | DISTANCE TO REMOVE ROTOR: mm |  |  |  |  |  |  |
| 23 | ROTOR CIRCUIT REACTANCE X2: |  |  |  |  |  |  |  |  | NET WEIGHT: 5100±5% Kg |
| 24 | MAGNETIZING REACTANCE XM: |  |  |  |  |  |  |  |  | SHIPPING WEIGHT: Kg |
| 25 | STATOR CIRCUIT RESISTANCER1 : |  |  |  |  |  |  |  |  | ROTOR WEIGHT: Kg |
| 26 | ROTOR CIRCUIT RESISTANCE R2 : |  |  |  |  |  |  |  |  | MAX. ERECTION WEIGHT: Kg |
| 27 | CORE LOSSES RESISTANCE RC : ……. Ω |  |  |  | STARTING: (Note 8) |  |  |  |  |  |  |
| 28 | ROTOR RUNNING |  |  |  | [ X ] DIRECT ON LINE [ ] REDUCED VOLTAGE |  |  |  |  |  |  |
| 29 | RESISTANCE …………………… REACTANCE: |  |  |  | %TAP:…………………………… |  |  |  |  |  |  |
| 30 | OPEN CIRCUIT TIME CONSTANT (T'do): |  |  |  | [ ] LOADED [ ] UNLOADED |  |  |  |  |  |  |
| 31 | TRANSIENT SHORT CIRCUIT TIME CONSTANT (T"d): |  |  |  | [ ] N DESIGN [ ] NY DESIGN |  |  |  |  |  |  |
| 32 | D.C. SHORT-CIRCUIT TIME CONSTANT (Ta): |  |  |  |  |  |  |  |  |  |  |
| 33 | EFFICIENCY, CURRENT AND POWER FACTOR AS FUNCTION OF LOAD |  |  |  |  |  |  | LOCKED ROTOR POWER FACTOR: ~25 % |  |  |  |
| 34 | LOAD% 100 75 50 |  |  |  | ALLOWABLE LOCKED ROTOR WITHSTAND TIME |  |  |  |  |  |  |
| 35 | EFFICIENCY % /PF 96,1 /0.9 96,3/0.89 95,8/0.84 |  |  |  | VOLTAGE % 100 80 |  |  |  |  |  |  |
| 36 | CURRENT A 150A 113A 80A |  |  |  | COLD: 35s ~ 50s |  |  |  |  |  |  |
| 37 | POWER FACTOR % 0,90 0,89 0,84 |  |  |  | HOT: 18s ~ 25s |  |  |  |  |  |  |

| G: MOTOR FEATURES |  |  |  |
| --- | --- | --- | --- |
| 1 | INSULATION CLASS: [X] F TEMPERATURE RISE AS PER: (Note 20) [X] CLASS B |  |  |
| 2 | MOTOR TYPE: |  | DC EXCITATION |
| 3 | [ X ] SQUIRREL CAGE [ ] BRUSH-LESS |  | kW REQUIRED: |
| 4 | [ ] SLIP RING [ ] SYNCHRONOUS |  | V REQUIRED: |
| 5 | DRIVE SYSTEM: |  | [ ] BY PURCHASER: |
| 6 | [X] DIRECTED CONNECTED [ ] GEAR |  | [ ] BY MANUFACTURER: |
| 7 | [ ] OTHERS ………………………………………………… |  | DESCRIPTIONS: |
| 8 | BEARING: (Note 9) |  |  |
| 9 | DRIVE END BEARING: |  | NON-DRIVE END BEARING: |
| 10 | BEARING TYPE: Sleeve bearings with self-lubrication |  | VARIABLE SPEED DRIVE: (Note 10) |
| 11 | LUBRIFICATION: [X] OIL VG 22 (ISO 3448) [ ] GREASE |  | [ ] FOR STARTING |
| 12 | LUBE OIL REQUIRED: 3 LITRER FOR EACH BEARING |  | [ ] FOR CONTINOUS VARIABLE SPEED |
| 13 | BEARING TEMPERTURE INDICATORS: |  | [ ] OTHERS: |
| 14 | [ ] N.O. CONTACTS [ ] N.C. CONTACTS |  | BEARING TEMPERTURE DETECTORS (Note 11) |
| 15 | [X] SET AT 95°C FOR ALARM [ ] THERMISTORS [X] RESISTANCE TEMP. DETECTOR: PT100 |  |  |
| 16 | [X] SET AT 100°C FOR SHUTDOWN |  | NUMBERING PER BEARING: |
| 17 | [ ] DESCRIPTIONS | [ ] RESISTANCE MATERIALS: Resistance value at 0°C is 100Ω / Platinum |  |
| 18 | WINDING TEMPERATURE DETECTORS: (Note 11) |  |  |
| 19 | [ ] THERMISTOR: NUMBER FOR PHASE N° |  | TEMPERATURE SWITCH: [ ] YES [X] NO |
| 20 | [ X ] TEMPERATUER COEFFICIENT (PT100) 6 x RTD's Pt100 (TWO PER PHASE) |  | RESISTANCE TEMPERATURE DETECTORS: No./Phase 2 |
| 21 | [ ] NEG. TEMPERATURE COEFFICIENT |  | [ ] RESISTANCE MATERIALS Platinum [ ] OHM 100 |
| 22 | SELECTOR SWITCH AND INDICATOR BY: |  | [ ] MAX. STATOR WINDING TEMPERATURE: |
| 23 | [ ] PURCHASER [ ] MANUFACTURER |  | ALARM: 135°C SHUTDOWN: 140°C |
| 24 | FEEDING CABLE(S): 3C-185mm2 (1 RUN) |  |  |
| 25 | CABLE TYPE: (CU XLPE INSULATED, ARMOURED, PVC JACKETED) |  |  |
| 26 | VIBRATION: (Note 12) |  | MOTOR DIFFERENTIAL PROTECTION: (Note 13) NOT APPLICABLE FOR P<1500KW |
| 27 | [X] VIBRATION GRADE “A”[ ] VIBRATION GRADE “B” |  | [ ] SELF BALANCED |
| 28 | [ ] VIBRATION TRANSDUCERS: N/A |  | [ ] START POINT CT-METHOD |
| 29 | MAKE: ………………………………………………………………… |  | [ ] CT DESCRIPTION: |
| 30 | [ X ] KEYPHASER LOCATION: On Motor Shaft N/A |  |  |
| 31 | [ X ] WIRING UP TO A DEDICATED JUNCTION BOX |  |  |
| 32 | TEWAC & TEIGF MOTORS |  |  |
| 33 | COOLING WATER REQUIRED: ……………………… TEMPERATURE RAISE: ……………………………………………… |  |  |
| 34 | PRESSURE DROP: …………………………………………… |  |  |
| H: TERMINAL BOX & COUPLING (Note 14) |  |  |  |
| 1 | MAIN TERMINAL BOXES (VDE): |  | Connections possible from directions 2A, 2B, 2C and 2D |
| 2 | EXECUTION: Ex eb IIC IP66 |  |  |
| 3 | LOCATION: [X] RIGHT [ ] LEFT |  |  |
| 4 | CABLE ENTRY: NO. 1 HOLE(S) M80 |  |  |
| 5 | THREADED: ISO M |  |  |
| 6 | AUX. TERMINAL BOXES (VDE): Two Boxes (Space heater&RTDs) |  |  |
| 7 | EXECUTION: Ex eb IIC IP66 |  |  |
| 8 | LOCATION: [X] RIGHT [ ] LEFT |  |  |
| 9 | CABLE ENTRY: 1xM20 (Space Heater) + 1xM32 (Windings RTDs) |  |  |
| 10 | THREADED: ISO M20 1xM25 bearing RTDs |  |  |
| 1 | STAR POINT TERMINL BOX (VDE) |  | COUPLING: |
| 2 | EXECUTION: |  | SUPPLIED BY: |

| I: ACCESSORIES AND VARIOUS |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 1 | SPACE HEATERS:N°: POWER: 400 W RATED VOLTAGE: [X]230 V (<3kW) [ ] 400 V (≥3kW) (Note21) |  |  |  |  |
| 2 | NAME PLATES LANGUAGE: ENGLISH Indication as per Std + Degree of Protection |  |  |  |  |
| 3 | EXTERNAL COLOUR: RAL 5010 (GENTIAN BLUE) TYPE: Qty PAINTING SPECIFICATION: (Note 15) |  |  |  |  |
| 4 | [ ] VIBRATION DETECTOR AND MONITORING N/A @ @ |  |  |  |  |
| 5 | [ ] COOLING AIR TEMPERATURE DETECTORS @ @ |  |  |  |  |
| 6 | [ ] WATER LEAKAGE DETECTOR (COOLING SYSTEM) N/A @ @ |  |  |  |  |
| 7 | [ ] CONTROL FLOW SWITCH @ @ |  |  |  |  |
| 8 | [ ] STAR POINT TERMINAL BOX @ @ |  |  |  |  |
| 9 | [ ] INTERNAL AIR FILTER |  |  |  |  |
| 10 | [ ] AXIALLY-MOUNTED SPEEDOMETER DYNAMO (IF NECESSARY) |  |  |  |  |
| 11 | [ ] ACCESSORIES |  |  |  |  |
| 12 | [ ] SUN SHADES CANOPY @ @ |  |  |  |  |
| 13 | [X] LIFTING EYES @ @ |  |  |  |  |
| 14 | [ ] DRAIN PLUG @ @ |  |  |  |  |
| 15 | [X] EARTHING BOLT @ @ |  |  |  |  |
| 16 | [ ] CABLE GLANDS @ @ |  |  |  |  |
| 17 | AIR FILTER @ |  |  |  |  |
| 18 | [ ] DIFFERENTIAL PRESSURE SWITCH |  |  |  |  |
| 19 | [ ] TYPE: ………………………………………………….. |  |  |  |  |
| J: SITE CONDITION (See Spec. DPC-EL-SPC-0001) |  |  |  |  |  |
| 1 | INSTALLATION: [ ] INDOOR [ X ] OUTDOOR |  | USE OF CANOPY REQUIRED: [ ] YES [ ] NO |  |  |
| 2 | MAX. AMBIENT TEMPERATURE: + 48°C |  | MIN. AMBIENT TEMPERATURE: - 4°C |  |  |
| 3 | DESIGN TEMPERATURE: + 48°C |  | EQUIPMENT EXPOSED TO SUNLIGHT: [ X ] (Note 6) |  |  |
| 4 | UNUSUAL CONDITIONS:(Note 16)[ ] DUST[ ]FUMES [ X ]OTHERS: |  |  |  | BAROMETRIC PRESSURE (Avg): 914 mbar |
| 5 | HEIGH ABOVE SEA LEVEL: 915 m |  | MAX. HUMIDITY % AT -°C: 100% |  |  |
| K: MATERIAL TYPE |  |  |  |  |  |
| 1 | ROTOR CAGE BARS: |  | INTERNAL OR EXTERNAL FANS / FAN GUARD: |  |  |
| 2 | STATOR WINDING: |  | SHAFT: |  |  |
| 3 | TERMINAL BOXES: |  | BEARING ELEMENTS: |  |  |
| 4 | NAME PLATE: |  | NUT & BOLTS: |  |  |
| L: TESTS |  |  |  |  |  |
| 1 | ROUTINE TESTS: (Note 17) |  | TYPE TESTS: (Note 18) |  |  |
| 2 | [ X ] RESISTANCE CIRCUITS |  | [ X ] ON LOAD TEST ACCORDING TO: IEC 60034-2 |  |  |
| 3 | [ X ] NO LOAD TEST |  |  | [ ] TYPE TEST REQUIRED BY RELEVANT STANDARD FOR HAZARDOUS MOTORS AS PER IEC |  |
| 4 | [ X ] SHORT CIRCUIT TEST |  |  |  |  |
| 5 | [ X ] MEASUREMENT OF VIBRATION AND SOUND LEVEL |  | [ X ]TYPE TEST FOR NON HAZARDOUS MOTORS AS PER IEC STANDARDS. |  |  |
| 6 | [ ] OVER SPEED TEST | HIGH-VOLTAGE TEST AND INSULATION RESISTANCE BEFORE AND AFTER [ X ] HEAT RUN |  |  |  |
| 7 | [ X ] WINDING INSULATION TEST |  | [ X ] FULL LOAD HEAT RUN |  |  |
| 8 | [ X ] INSULATION RESISTANCE |  | [ X ] MEASUREMENT OF SLIP AT FULL LOAD |  |  |
| 9 | [ ] FOR Ex MOTORS ROUTINE TEST REQUIRED BY RELAVANT STD. |  | [X ] MEASUREMENT TO ALLOW CALCULATION OF PULL-OUT TORQUE |  |  |
| 10 | [ X ] CHECKING OF PROTECTION DEGREE |  | MEASUREMENT TO ALLOW CALCULATION OF EFFICIENCY AT FULLY, [X ] THREE-QUARTER AND HALF LOAD |  |  |
| 11 | [ X ]MEASUREMENT OF WINDING RESISTANCE (COLD) |  | [ X ] HIGH-VOLTAGE AND CONTINUITY TESTS ON BUILT-IN TEMPERATURE DETECTORS |  |  |
| 12 | [ X ] MEASUREMENT TO ALLOW CALCULATION OF LOCKED ROTOR ADDITIONAL TESTS CURRENT AND TORQUE |  |  |  |  |
| 13 | [ X ] HIGH-VOLTAGE TEST [ ] AIR GAP MEASURING [ X ] VISUAL INSPECTION AND DIMENSIONAL CHECK |  |  |  |  |
| 14 | [ ] ROTOR INERTIA MEASURING [ X ] REVIEW OF TEST CERTIFICATE |  |  |  |  |

| M: NOTES |  |
| --- | --- |
| 1 | VENDOR SHALL FILL IN THE PRESENT DATA SHEET FORM SEPARATELY FOR EACH MOTOR. |
| 2 | AS PER IEC 60034-7 "CLASSIFICATION OF TYPES OF CONSTRUCTION AND MOUNTING ARRANGEMENT (IM CODE)". |
| 3 | AS PER SELECTION OF EQUIPMENT FOR CLASSIFIED HAZARDOUS AND UNCLASSIFIED AREAS SPECIFICATION DPC-EL-SPC-0004.ALSO MECHANICAL PROTECTION DEGREE ACCORDONG TO IEC 60034-5 & IEC 60529. |
| 4 | STARTING CURRENT TO RATED CURRENT RATIO SHALL NOT EXCEED THE FOLLOWING VALUES: - MOTORS RATED POWER LESS THAN 2.000 KW: 5,5 IN - MOTORS RATED POWER HIGHER THAN OR EQUAL TO 2.000 KW: 4,0 IN |
| 5 | SERVICE FACTOR GREATER THAN 1.0 ARE PERMITTED ONLY WHEN SPECIFIED IN THE DATA SHEET. |
| 6 | OUTDOOR LOCATIONS ELECTRICAL EQUIPMENT SHALL BE SUITABLE FOR THE ENVIRONMENTAL CONDITIONS (E.G. DUST, MOISTURE, SNOW OR RAIN) WITH ADDITIONAL PROTECTION PROVIDED (E.G. RAIN SHIELDS, SUN SHIELDS) WHERE REQUIRED. |
| 7 | SUPPLIER OF ALL EQUIPMENT SHALL BE INCLUDED. |
| 8 | STARTING PERFORMANCE OF SINGLE-SPEED THREE-PHASE CAGE INDUCTIONS MOTORS ACCORDING TO IEC 60034-12. MOTORS SHALL BE SUITABLE TO START AND ACCELERATE THE LOAD AT 80% OF RATED VOLTAGE AT ITS TERMINALS AND CAPABLE TO WITHSTANDING ANY TRANSIENT TORQUE DUE TO THE POWER NETWORK. |
| 9 | BEARING SHALL BE IN COMPLIANCE WITH THE REQUIREMENTS OF ISO 281. MOTORS FOR VERTICAL PUMPS, INCLUDING IN LINE SHALL HAVE RAIN PROTECTION COVER.ALSO VERTICAL MOTORS SHALL HAVE THRUST BEARINGS SUITABLE FOR THE LOAD IMPOSED BY THE DRIVEN MACHINERY; HOUSING OF SLEEVE BEARING SHALL BE EQUIPPED WITH SIGHT-FEED OILER OR SIGHT GAUGE MARKED WITH PROPER OIL LEVEL. |
| 10 | IN CASE OF MOTOR WITH VARIABLE SPEED DRIVE (VSD), VENDOR SHALL FILL IN ALSO VSD DAT SHEET.ONLY FOR VARIABLE SPEED MOTORS. IF SYNCHRONOUS MOTORS HAVE TO BE STARTED VIA STARTING CONVERTER (DEPENDING ON THE NETWORK CONDITIONS) THE MOTOR DESIGN SHALL BE ACCORDINGLY AND SHALL BE EXECUTED IN CLOSE COORDINATION WITH THE VSD (VARIABLE SPEED DRIVES) SYSTEM DESIGN. |
| 11 | RTDs SHALL BE PROVIDED FOR MV MOTORS (≥ 150kW) AND WHERE REQUIRED BY MACHINE MONITORING SYSTEM. A MINIMUM OF THREE (ONE PER PHASE) DETECTORS SHALL BE PROVIDED BETWEEN THE COIL SIDES TO MEASURE THE WINDING TEMPERATURE AND THREE (ONE PER PHASE) AT THE BASE OF THE SLOTS TO MEASURE CORE TEMPERATURE, EACH PLACED 120° APART. SLEEVE BEARINGS FOR MV-MOTORS SHALL BE EQUIPPED WITH A DOUBLE RESISTANCE TEMPERATURE DETECTOR OF THE PT 100, 3 OR 4 WIRE TYPE. |
| 12 | LIMITS OF MAXIMUM MECHANICAL VIBRATION MAGNITUDE ACCORDING TO IEC 60034-14. |
| 13 | DIFFERENTIAL PROTECTION SHALL BE PROVIDED ONLY FOR MOTOR LARGER THAN 1500 kW. MOTORS SHALL INCLUDE THE SIX CURRENT TRANSFORMERS FOR DIFFERENTIAL PROTECTION (THREE CT’S INSIDE THE STAR POINT TERMINAL BOX AND THREE CT’S FOR THE INSTALLATION IN THE FEEDING UNIT).THE ENCLOSURE TYPE OF THE TERMINAL BOX SHALL NOT BE LOWER THAN THE MAIN MOTOR ENCLOSURE. |
| 14 | 1- THE BOX SHALL BE OVERSIZED AND COMPATIBLE WITH THE DIMENSIONS OF POWER CABLES AND RELEVANT ACCESSORIES (LUGS AND TERMINATIONS), SO LOCATED AS TO ENSURE AN EASY SET-UP OF CABLE ENDS AND ACCESS TO TERMINALS. 2- THERE SHALL BE SEPARATE TERMINAL BOXES FOR MAINS, SPACE HEATER AND MEASURING SENSORS FOR TEMPERATURE OF BEARINGS AND VIBRATIONS. SEPARATED BOXES LOCATED ON THE OPPOSITE SIDE OF THE MAIN ONE. 3- ALL INLET HOLES SHALL BE PROVIDED WITH THREADED PLUGS SUITABLE FOR THE TYPE OF PROTECTION OF THE TERMINAL BOXES. 4-MAIN BOX FOR 6 KV MOTORS WILL BE ALSO CAPABLE TO ACCOMMODATE THE SURGE ARRESTERS. 5-GASKETS SHALL BE LOCATED IN SUITABLE SEATS AND SHALL BE OF MATERIALS WITH AGE-RESISTING CHARACTERISTICS AND ELASTIC PROPERTIES PRACTICALLY UNAFFECTED BY TEMPERATURE VARIATIONS OCCURRING DURING MOTOR RUNNING. 6-FOR MOTOR RATED POWER EQUAL TO OR HIGHER THAN 3.5 KW, A STAR POINT TERMINAL BOX SHALL BE INCLUDED |

| 15 | AS PER PAINTING SPECIFICATION DPIC9812-000-000-PI-JSD-2300-0001. |
| --- | --- |
| 16 | DUST OVER THE FLAT TERRAIN AND A HIGH CORROSION IN THIS AREA MUST BE CONSIDERED. THE PRESENCE OF CORROSIVE GAS MIXTURES AND POLLUTED RAINFALL MUST BE CONSIDERED. MOTORS CAN BE DIRECTLY EXPOSED TO SUNLIGHT AND TO WEATHER INJURY, WITHOUT ANY ADDITIONAL PROTECTION. |
| 17 | FOR FURTHER DETAILS REGARDING ROUTINE TESTS AND FOR WITNESS TESTS REFER TO RELATED SPECIFICATION. |
| 18 | TYPE TEST SHALL BE QUOTED SEPARATELY IN THE BID. |
| 19 | THE SUPPLY SHALL BE IN COMPLIANCE WITH JOB SPECIFICATION FOR SUPPLY MEDIUM VOLTAGE MOTORS DPC-EL-SPC-0020. |
| 20 | WINDING INSULATION PHASE TO PHASE AND PHASE TO EARTH, SHALL BE CLASS F NON HYGROSCOPIC WITH A 85 °K TEMPERATURE RISE MEASURED BY SLOT-EMBEDDED RESISTANCE TEMPERATURE DETECTOR ( RTD ) AND 80 °K AVERAGE TEMPERATURE RISE ( ACCORDING TO IEC 60034 ) OVER 40 °C AMBIENT MAXIMUM AT RATED OUTPUT ( 1.0 SERVICE FACTOR RATING ). |
| 21 | LEAD OF SPACE HEATERS, CONTROL OR DETECTION SIGNAL SHALL BE TERMINATED IN TERMINAL BOXES SEPARATE FROM THAT HAVE BEEN USED FOR THE MAIN POWER LOAD TERMINAL BOXES. SPACE HEATERS SHALL BE PROVIDED FOR MOTORS ABOVE 150KW. |
| 22 | THE MOTOR TORQUES DURING STARTING (LOCKED-ROTOR TORQUE, PULL-UP TORQUE, BREAKDOWN TORQUE), AT RATED FREQUENCY AND AT MINIMUM VOLTAGE ALLOWED, SHALL ENSURE A CORRECT STARTING, ACCORDING TO IEC 60034 UNLESS LOAD TORQUE REQUIRES MOTOR WITH SPECIAL CHARACTERISTICS. |
| 23 | VENDOR SHALL SUPPLY THE REQUIRED ELECTRICAL CERTIFICATIONS AND DOCUMENTS AS PER SPECIFICATION (DPC-EL-SPC-0020). |
| 24 | MANUFACTURER SHALL ALSO QUOTE SEPARATELY, SUPERVISION ON SITE FOR COMMISSIONING AND START UP OF THE MOTOR |
| 25 | INFORMATION TO BE COMPLETED BY MANUFACTURER INFORMATION TO BE COMMUNICATED OR CONFIRMED LATER |

Note:

Motor need to be prepurging before start:

Prepurging volume: 37.5 m3 for minimum 15 minute (flow rate minimum 150 m3/h)