## Sheet1
SINGLE STAGE SCREW COMPRESSOR :
DATE : |  | 2020-09-11 | design | 1750 | kW
MODEL : |  | PPN320L**-ME | normal | 1200 | kW
REFRIGERANT : |  | PROPYLENE | minimum | 100 | kW
RECOMMENDED PORT : |  | M
BOOSTER : |  | N
Vi : | [-] | 4.59
COMPRESSION RATIO : | [-] | 8.12
CAPACITY : | [kW] | 1813.6
CAPACITY : | [TR] | 515.7
ABSORBED POWER : | [kW] | 1160.7
DRIVE SHAFT SPEED : | [min-1] | 2950
COMPRESSOR SPEED : | [min-1] | 2950
INDICATOR POSITION : | [%] | 100
CONDENSING TEMP. : | [degC] | 48
EVAPORATIVE TEMP. : | [degC] | -25
SUCTION SUPERHEAT : | [degC] | 0
LIQUID SUBCOOLING : | [degC] | 0
SUCTION TEMP. : | [degC] | -25
OIL SUPPLY TEMP. : | [degC] | 50
SUCTION PRESS. : | [MPaA] | 0.246
DISCHARGE PRESS. : | [MPaA] | 2
OIL SUPPLY PRESS. : | [MPaA] | 2.19
SUCTION PRES. DROP : | [MPa] | 0.01
DISCHARGE PRES. DROP : | [MPa] | 0.03
SWEPT VOLUME : | [m3/h] | 4740
LOAD(SUCTION VOL. FLOW RATE) : | [%] | 100
DISCHARGE TEMP. : | [degC] | 80.3
REFRIG. FLOW RATE SUC. : | [m3/h] | 3900
REFRIG. FLOW RATE DIS. : | [m3/h] | 792
REFRIG. FLOW RATE SUC. : | [kg/h] | 21030
REFRIG. FLOW RATE DIS. : | [kg/h] | 28010
INJECT. OIL FLOW RATE : | [L/min] | -
LUB. OIL FLOW RATE : | [L/min] | 240
*TOTAL* OIL FLOW RATE : | [L/min] | 240
OIL HEAT REJECTION : | [kW] | 205.5
OIL SPEC HT : | [J/kgK] | 1930
OIL DENSITY : | [kg/m3] | 880
COP : | [-] | 1.56
--- SUPER HEAT is NOT counted in refrigeration capacity ---
--- WITH WATER COOLED OIL COOLER ---
--- WITH LIQUID SUBCOOLER ---
INTERMED. TEMP. : | [degC] | 11.3
INTERMED. PRESS. : | [MPaA] | 0.807
INTERMED. SUPERHEAT : | [degC] | 0
LIQUID APPROACH TEMP. : | [degC] | 5
REFRIG. FLOW RATE : | [m3/h] | 411
REFRIG. FLOW RATE : | [kg/h] | 6984
HEAT REJECTION : | [kW] | 502.2
--- NO OIL INJECTION ---
--- When choosing the motor set a safety factor of more than 10% for the brake power. ---
--- UD series excluding 125 and 400 can support only cast steel specifications.
--- Please check carefully the operating range. ---
--- Reference temperature : Dew Point ---
! Absorbed power is out of limit. (Max. 2950min-1:1020kW / 3550min-1:1228kW)
! All data herein is for reference only.
! Content is subject to change without notice.
*** MYCOMW2020_ver.1.1 compressor performance table is valid until the end of March, 2021. ***