## Load List
Gachsaran Polymer Industries Company HDPE Plant
P.o. No.: GPIC-PT-MA-PO-000-3029
Document Title: ELECTRICAL LOAD LIST
Rev.: 00
|  |  | Document No.: VD-GPIC-MA-3029-3029-0060 | [8 empty] | Page: 3 of 3
ITEM NO. | Tag No. | Description |  | Voltage (V) (1) | Mechanical (Shaft) Power (kW) (2) | Rated Power (kW) (3) | Duty (C/I/S) (4) | Source Type (N/E/V) (5) | Power Factor (6) | Efficiency (%) (7) | Rated Current (A) (8) | Load Factor (9) | Sync. Speed (rpm) (10) | Absorbed Active Power (kW) (11) | Absorbed Reactive Power (kVAR) (12) | Remark
1 | CM-6101A | MOTOR FOR REFRIGERANT COMPRESSOR A |  | 6000 | 1089 | 1250 | C | N | 0.87 | 95.8 | 144 | 0.8712 | 3000 | 1136.7432 | 644.2221
2 | CM-6101A-SH | SPACE HEATER FOR MOTOR OF REFRIGERANT COMPRESSOR A |  | 230 | - | 0.8 | S | N | 1 | 100 | 3.4783 | 1 | - | 0.8 | 0
3 | PM-6111A | OIL PUMP MOTOR A FOR REFRIGERANT COMPRESSOR A |  | 400 | 9.3 | 11 | C | N | 0.85 | 90.6 | 20.6 | 0.84545 | 1500 | 10.2649 | 6.3616
4 | PM-6111B | OIL PUMP MOTOR B FOR REFRIGERANT COMPRESSOR B |  | 400 | 9.3 | 11 | I | N | 0.85 | 90.6 | 20.6 | 0.84545 | 1500 | 10.2649 | 6.3616
5 | EH-6101 | OIL HEATER FOR REFRIGERAN PACKAGE |  | 400 | - | 9 | I | N | 1 | 100 | 12.9904 | 1 | - | 9 | 0
| CM-6101B | MOTOR FOR REFRIGERANT COMPRESSOR B |  | 6000 | 1089 | 1250 | C | N | 0.87 | 95.8 | 144 | 0.8712 | 3000 | 1136.7432 | 644.2221
6 | CM-6101B-SH | SPACE HEATER FOR MOTOR OF REFRIGERANT COMPRESSOR B |  | 230 | - | 0.8 | S | N | 1 | 100 | 3.4783 | 1 | - | 0.8 | 0
7 | UCP-6101 | NON-UPS POWER SUPPLY FOR UCP |  | 230 | - | 0.6 | C | E | 0.95 | 100 | 2.746 | 1 | - | 0.6 | 0.19721
8 | UCP-6101 | UPS POWER SUPPLY 1 FOR UCP |  | 110 | - | 1 | C | V | 0.95 | 100 | 9.5694 | 1 | - | 1 | 0.32868
9 | UCP-6101 | UPS POWER SUPPLY 2 FOR UCP |  | 110 | - | 1 | S | V | 0.95 | 100 | 9.5694 | 1 | - | 1 | 0.32868
DEFINITIONS & NOTES:
(4): C: CONTINIOUS I: INTERMITTENT S: STANDBY
(5): N: NORMAL E: EMERGENCY (FROM DIESEL GENERATOR) V: VITAL (FROM UPS)
LOAD FACTOR (9) = (2) / (3)
ABSORBED ACTIVE POWER kW (11) = (2) / (7)
ABSORBED REACTIVE POWER kVAR (12) = (11) * TAN (ACOS (6) )