## Table 1
STATES
TAG | SERVICE | PID DWG No. | TYPE | FROM | TO | DESCRIPTION | Engineering units | LOCATION | JB No. | SIGNAL CATEGORY | SIGNAL | RELAY OUTPUT | POWER SUPPLY | TYPE | SERIAL | IS/NIS | RACK | SLOT | CHANNEL | STATES'0' | STATES'1'
Card Type: Digital IN/ 16
TAG | SERVICE | PID DWG No. |  |  |  | DESCRIPTION |  | LOCATION | JB No. | SIGNAL CATEGORY | SIGNAL TYPE | RELAY OUTPUT | POWER SUPPLY |  |  |  | RACK | SLOT | CHANNEL
XA- 61199 | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | UCP-6101 | PLC | UPS AC SUPPLY 1 SURGE PROTECTION OK |  | UCP-6101 | UCP-6101 | DI | 24VDC | - | PW400 | H |  | NIS | 2 | 2 | 0 | OFF | ON
XA- 61198 | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | UCP-6101 | PLC | UPS AC SUPPLY 2 SURGE PROTECTION OK |  | UCP-6101 | UCP-6101 | DI | 24VDC | - | PW400 | H |  | NIS | 2 | 2 | 1 | OFF | ON
XA- 61190 | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | UCP-6101 | PLC | LOGIC POWER SUPPLY # 1 OK |  | UCP-6101 | UCP-6101 | DI | 24VDC | - | PW400 | H |  | NIS | 2 | 2 | 2 | OFF | ON
XA- 61191 | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | UCP-6101 | PLC | LOGIC POWER SUPPLY # 2 OK |  | UCP-6101 | UCP-6101 | DI | 24VDC | - | PW400 | H |  | NIS | 2 | 2 | 3 | OFF | ON
XA- 61192 | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | UCP-6101 | PLC | I/O POWER SUPPLY # 1 OK |  | UCP-6101 | UCP-6101 | DI | 24VDC | - | PW400 | H |  | NIS | 2 | 2 | 4 | OFF | ON
XA- 61193 | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | UCP-6101 | PLC | I/O POWER SUPPLY # 2 OK |  | UCP-6101 | UCP-6101 | DI | 24VDC | - | PW400 | H |  | NIS | 2 | 2 | 5 | OFF | ON
HS-61161 | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | UCP-6101 | PLC | ESD |  | UCP-6101 | UCP-6101 | DI | 24VDC | - | PW400 | H |  | NIS | 2 | 2 | 6
[6 empty] | SPARE | [10 empty] | 2 | 2 | 7
HS-C6101A | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | ESD / DCS | UCP-6101 | ESD |  | ESD / DCS | LCP-6101A | DI | 24VDC | DRY CONTACT | PW400 | H |  | NIS | 2 | 2 | 8 | OFF | ON
HST-C6101A | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | LCP-6101A | UCP-6101 | COMPRESSOR -A- LOCAL START PB |  | COMP A SKID | LCP-6101A | DI | 24VDC | DRY CONTACT | PW400 | H |  | NIS | 2 | 2 | 9 | OFF | ON
HSP-C6101B | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | LCP-6101A | UCP-6101 | COMPRESSOR -A- LOCAL STOP PB |  | COMP A SKID | LCP-6101A | DI | 24VDC | DRY CONTACT | PW400 | H |  | NIS | 2 | 2 | 10 | OFF | ON
[6 empty] | SPARE | [10 empty] | 2 | 2 | 11
HST-C6101B | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | LCP-6101B | UCP-6101 | COMPRESSOR -B- LOCAL START PB |  | COMP -B- SKID | LCP-6101B | DI | 24VDC | DRY CONTACT | PW400 | H |  | NIS | 2 | 2 | 12 | OFF | ON
HSP-C6101B | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | LCP-6101B | UCP-6101 | COMPRESSOR -B- LOCAL STOP PB |  | COMP -B- SKID | LCP-6101B | DI | 24VDC | DRY CONTACT | PW400 | H |  | NIS | 2 | 2 | 13 | OFF | ON
ESD-61010 | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | DCS | PLC | ESD |  | DCS | UCP-6101 | DI | 24VDC | DRY CONTACT | PW400 | H |  | NIS | 2 | 2 | 14 | OFF | ON
[6 empty] | SPARE | [10 empty] | 2 | 2 | 15
Card Type: Digital IN/ 16
TAG | [5 empty] | DESCRIPTION |  | LOCATION | JB No. | SIGNAL CATEGORY | SIGNAL TYPE | RELAY OUTPUT | POWER SUPPLY |  |  |  | RACK | SLOT | CHANNEL
HSLR-C6101A | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | LCP-6101A | UCP-6101 | COMPRESSOR -A- LOCAL -REMOTE SELECTOR |  | COMP -B- SKID | LCP-6101B | DI | 24VDC | - | PW400 | H |  | NIS | 2 | 3 | 0 | OFF | ON
HSLR-C6101B | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | LCP-6101B | UCP-6101 | COMPRESSOR -B- LOCAL -REMOTE SELECTOR |  | COMP -B- SKID | LCP-6101B | DI | 24VDC | - | PW400 | H |  | NIS | 2 | 3 | 1 | OFF | ON
[6 empty] | SPARE |  |  |  | DI | 24VDC |  | PW400 |  |  |  | 2 | 3 | 2
[6 empty] | SPARE |  |  |  | DI | 24VDC |  | PW400 |  |  |  | 2 | 3 | 3
[6 empty] | SPARE |  |  |  | DI | 24VDC |  | PW400 |  |  |  | 2 | 3 | 4
[6 empty] | SPARE |  |  |  | DI | 24VDC |  | PW400 |  |  |  | 2 | 3 | 5
[6 empty] | SPARE |  |  |  | DI | 24VDC |  | PW400 |  |  |  | 2 | 3 | 6
[6 empty] | SPARE |  |  |  | DI | 24VDC |  | PW400 |  |  |  | 2 | 3 | 7
ZSH-61111 | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | JB-UID-61111 | UCP-6101 | COMPRESSOR -A- SLIDE VALVE 100% |  | COMP -A- SKID | JB-UID-61111 | DI | 24VDC | DRY CONTACT | PW400 | H |  | IS | 2 | 3 | 8 | OFF | ON
ZSL-61111 | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | JB-UID-61111 | UCP-6101 | COMPRESSOR -A- SLIDE VALVE 0% |  | COMP -A- SKID | JB-UID-61111 | DI | 24VDC | DRY CONTACT | PW400 | H |  | IS | 2 | 3 | 9 | OFF | ON
ZSH-61121 | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | JB-UID-61121 | UCP-6101 | COMPRESSOR -B- SLIDE VALVE 100% |  | COMP -B- SKID | JB-UID-61121 | DI | 24VDC | DRY CONTACT | PW400 | H |  | IS | 2 | 3 | 10 | OFF | ON
ZSL-61121 | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | JB-UID-61121 | UCP-6101 | COMPRESSOR -B- SLIDE VALVE 0% |  | COMP -B- SKID | JB-UID-61121 | DI | 24VDC | DRY CONTACT | PW400 | H |  | IS | 2 | 3 | 11 | OFF | ON
[6 empty] | SPARE |  |  |  | DI | 24VDC |  | PW400 |  |  |  | 2 | 3 | 12
YSLH-6101B | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | MCC | UCP-6101 | COMPRESSOR -B- RUNNING |  | MCC | UCP-6101 | DI | 24VDC | DRY CONTACT | PW400 | H |  | NIS | 2 | 4 | 13 | OFF | ON
YSLF-6101B | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | MCC | UCP-6101 | COMPRESSOR -B- FAULT |  | MCC | UCP-6101 | DI | 24VDC | DRY CONTACT | PW400 | H |  | NIS | 2 | 4 | 14 | OFF | ON
[6 empty] | SPARE |  |  |  | DI | 24VDC |  | PW400 |  |  |  | 2 | 3 | 15
Card Type: Digital IN/ 16
TAG | [5 empty] | DESCRIPTION |  | LOCATION | JB No. | SIGNAL CATEGORY | SIGNAL TYPE | RELAY OUTPUT | POWER SUPPLY |  |  |  | RACK | SLOT | CHANNEL
YSLH-6101A | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | MCC | UCP-6101 | COMPRESSOR -A- RUNNING |  | MCC | UCP-6101 | DI | 24VDC | DRY CONTACT | PW400 | H |  | NIS | 2 | 4 | 0 | OFF | ON
YSLF-6101A | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | MCC | UCP-6101 | COMPRESSOR -A- FAULT |  | MCC | UCP-6101 | DI | 24VDC | DRY CONTACT | PW400 | H |  | NIS | 2 | 4 | 1 | OFF | ON
YSLH-EH6101 | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | MCC | UCP-6101 | OIL HEATER RUNNING |  | MCC | UCP-6101 | DI | 24VDC | DRY CONTACT | PW400 | H |  | NIS | 2 | 4 | 2 | OFF | ON
YSLF-EH6101 | Propylene | VD-GPIC-MA-3029-3029-0016 | BOOL | MCC | UCP-6102 | OIL HEATER - FAULT |  | MCC | UCP-6102 | DI | 24VDC | DRY CONTACT | PW400 | H |  | NIS | 2 | 4 | 3 | OFF | ON
YSLH-P6111A | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | MCC | UCP-6101 | PUMP P1A RUNNING |  | MCC | UCP-6101 | DI | 24VDC | DRY CONTACT | PW400 | H |  | NIS | 2 | 4 | 4 | OFF | ON
YSLF-P6111A | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | MCC | UCP-6101 | PUMP P1A - FAULT |  | MCC | UCP-6101 | DI | 24VDC | DRY CONTACT | PW400 | H |  | NIS | 2 | 4 | 5 | OFF | ON
YSLH-P6111B | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | MCC | UCP-6101 | PUMP P1B RUNNING |  | MCC | UCP-6101 | DI | 24VDC | DRY CONTACT | PW400 | H |  | NIS | 2 | 4 | 6 | OFF | ON
YSLF-P6111B | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | MCC | UCP-6101 | PUMP P1B - FAULT |  | MCC | UCP-6101 | DI | 24VDC | DRY CONTACT | PW400 | H |  | NIS | 2 | 4 | 7 | OFF | ON
[6 empty] | SPARE |  |  |  | DI | 24VDC |  | PW400 | H |  | NIS | 2 | 4 | 8
[6 empty] | SPARE |  |  |  | DI | 24VDC | - | PW400 |  |  |  | 2 | 4 | 9
[6 empty] | SPARE |  |  |  | DI | 24VDC |  | PW400 |  |  |  | 2 | 4 | 10
HS-C6101B | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | LCP-6101B | UCP-6101 | ESD |  | COMP -B- SKID | LCP-6101B | DI | 24VDC | DRY CONTACT | PW400 | H |  | NIS | 2 | 4 | 11 | OFF | ON
YLH-P6111A | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | UCP-6101 | LCP-6101A | PUMP P1A RUNNING |  | COMP -A- SKID | LCP-6101A | DI | 24VDC | DRY CONTACT | PW400 | H |  | NIS | 2 | 4 | 12 | OFF | ON
YL-P6111A | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | UCP-6101 | LCP-6101A | PUMP P1A - FAULT |  | COMP -A- SKID | LCP-6101A | DI | 24VDC | DRY CONTACT | PW400 | H |  | NIS | 2 | 4 | 13 | OFF | ON
YLH-P6111B | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | UCP-6101 | LCP-6101A | PUMP P1B RUNNING |  | COMP -A- SKID | LCP-6101A | DI | 24VDC | DRY CONTACT | PW400 | H |  | NIS | 2 | 4 | 14 | OFF | ON
YL-P6111B | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | UCP-6101 | LCP-6101A | PUMP P1B - FAULT |  | COMP -A- SKID | LCP-6101A | DI | 24VDC | DRY CONTACT | PW400 | H |  | NIS | 2 | 4 | 15 | OFF | ON
Card Type: Digital IN/ 16
TAG | [5 empty] | DESCRIPTION |  | LOCATION | JB No. | SIGNAL CATEGORY | SIGNAL TYPE | RELAY OUTPUT | POWER SUPPLY |  |  |  | RACK | SLOT | CHANNEL
HS-P6111A/B-A | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | LCP-6101A | UCP-6101 | LEAD/LAG - P1A - SELECTOR |  | COMP -A- SKID | LCP-6101A | DI | 24VDC | DRY CONTACT | PW400 | H |  | NIS | 2 | 5 | 0 | OFF | ON
HS-P6111A/B-B | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | LCP-6101A | UCP-6101 | LEAD/LAG - P1 - SELECTOR |  | COMP -A- SKID | LCP-6101A | DI | 24VDC | DRY CONTACT | PW400 | H |  | NIS | 2 | 5 | 1 | OFF | ON
HSLR-P6111A | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | LCP-6101A | UCP-6101 | HOA-HAND - PUMP 1A |  | COMP -A- SKID | UCP-6101 | DI | 24VDC | DRY CONTACT | PW400 | H |  | NIS | 2 | 5 | 2 | OFF | ON
HSLR-P6111A | Propylene | VD-GPIC-MA-3029-3029-0016 | BOOL | LCP-6101A | UCP-6102 | HOA-OFF - PUMP 1A |  | COMP -A- SKID | UCP-6102 | DI | 24VDC | DRY CONTACT | PW400 | H |  | NIS | 2 | 5 | 3 | OFF | ON
HSLR-P6111A | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | LCP-6101A | UCP-6101 | HOA-AUTO - PUMP 1A |  | COMP -A- SKID | UCP-6101 | DI | 24VDC | DRY CONTACT | PW400 | H |  | NIS | 2 | 5 | 4 | OFF | ON
HST-P6111A | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | LCP-6101A | UCP-6101 | PUMP 1A LOCAL START PB |  | COMP -A- SKID | UCP-6101 | DI | 24VDC | DRY CONTACT | PW400 | H |  | NIS | 2 | 5 | 5 | OFF | ON
HSP-P6111A | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | LCP-6101A | UCP-6101 | PUMP 1A LOCAL STOP PB |  | COMP -A- SKID | UCP-6101 | DI | 24VDC | DRY CONTACT | PW400 | H |  | NIS | 2 | 5 | 6 | OFF | ON
[6 empty] | SPARE |  |  |  | DI | 24VDC | - | PW400 |  |  |  | 2 | 5 | 7
HSLR-P6111B | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | LCP-6101A | UCP-6101 | HOA-HAND - PUMP 1B |  | COMP -A- SKID | UCP-6101 | DI | 24VDC | DRY CONTACT | PW400 | H |  | NIS | 2 | 5 | 8 | OFF | ON
HSLR-P6111B | Propylene | VD-GPIC-MA-3029-3029-0016 | BOOL | LCP-6101A | UCP-6102 | HOA-OFF - PUMP 1B |  | COMP -A- SKID | UCP-6102 | DI | 24VDC | DRY CONTACT | PW400 | H |  | NIS | 2 | 5 | 9 | OFF | ON
HSLR-P6111B | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | LCP-6101A | UCP-6101 | HOA-AUTO - PUMP 1B |  | COMP -A- SKID | UCP-6101 | DI | 24VDC | DRY CONTACT | PW400 | H |  | NIS | 2 | 5 | 10 | OFF | ON
HST-P6111B | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | LCP-6101A | UCP-6101 | PUMP 1B LOCAL START PB |  | COMP -A- SKID | UCP-6101 | DI | 24VDC | DRY CONTACT | PW400 | H |  | NIS | 2 | 5 | 11 | OFF | ON
HSP-P6111B | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | LCP-6101A | UCP-6101 | PUMP 1B LOCAL STOP PB |  | COMP -A- SKID | UCP-6101 | DI | 24VDC | DRY CONTACT | PW400 | H |  | NIS | 2 | 5 | 12 | OFF | ON
[6 empty] | SPARE |  |  |  | DI | 24VDC | - | PW400 |  |  | NIS | 2 | 5 | 13
[6 empty] | SPARE |  |  |  | DI | 24VDC |  | PW400 |  |  |  | 2 | 5 | 14
[6 empty] | SPARE |  |  |  | DI | 24VDC |  | PW400 |  |  |  | 2 | 5 | 15
STATES
TAG | SERVICE | PID DWG No. | TYPE | FROM | TO | DESCRIPTION | Engineering units | LOCATION | JB No. | SIGNAL CATEGORY | SIGNAL | RELAY OUTPUT | POWER SUPPLY | TYPE | SERIAL | IS/NIS | RACK | SLOT | CHANNEL | STATES'0' | STATES'1'
Card Type: Digital IN/ 16
Card Type: Digital OUT/ 16
TAG | [5 empty] | DESCRIPTION |  | LOCATION | JB No. | SIGNAL CATEGORY | SIGNAL TYPE | RELAY OUTPUT | POWER SUPPLY |  |  |  | RACK | SLOT | CHANNEL
YLH-6101B | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | UCP-6101 | LCP-6101A | COMPRESSOR -A- RUNNING |  | COMP SKID | LCP-6101A | DO | 24VDC | WET CONTACT | PW400 | H |  | NIS | 2 | 6 | 0 | OFF | ON
YL-6101B | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | UCP-6101 | LCP-6101A | COMPRESSOR -A- AVAILABLE/FAULT |  | COMP SKID | LCP-6101A | DO | 24VDC | WET CONTACT | PW400 | H |  | NIS | 2 | 6 | 1 | OFF | ON
YLH-6101B | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | UCP-6101 | LCP-6101B | COMPRESSOR -B- RUNNING |  | COMP SKID | LCP-6101A | DO | 24VDC | WET CONTACT | PW400 | H |  | NIS | 2 | 6 | 2 | OFF | ON
YL-6101B | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | UCP-6101 | LCP-6101B | COMPRESSOR -B- AVAILABLE/FAULT |  | COMP SKID | LCP-6101A | DO | 24VDC | WET CONTACT | PW400 | H |  | NIS | 2 | 6 | 3 | OFF | ON
[6 empty] | SPARE |  |  |  | DO | 24VDC |  | PW400 |  |  |  | 2 | 6 | 4
XA- 61195 | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | UCP-6101 | UCP-6101 | ENCLOSURE FANS ON/OFF - 1 |  | UCP-6101 | UCP-6101 | DO | 24VDC | WET CONTACT | PW400 | H |  | NIS | 2 | 6 | 5 | OFF | ON
[6 empty] | SPARE |  |  |  | DO | 24VDC |  | PW400 |  |  |  | 2 | 6 | 6
[6 empty] | SPARE |  |  |  | DO | 24VDC |  | PW400 |  |  |  | 2 | 6 | 7
[6 empty] | SPARE |  |  |  | DO | 24VDC |  | PW400 |  |  |  | 2 | 6 | 8
[6 empty] | SPARE |  |  |  | DO | 24VDC |  | PW400 |  |  |  | 2 | 6 | 9
[6 empty] | SPARE |  |  |  | DO | 24VDC |  | PW400 |  |  |  | 2 | 6 | 10
[6 empty] | SPARE |  |  |  | DO | 24VDC |  | PW400 |  |  |  | 2 | 6 | 11
[6 empty] | SPARE |  |  |  | DO | 24VDC |  | PW400 |  |  |  | 2 | 6 | 12
[6 empty] | SPARE |  |  |  | DO | 24VDC |  | PW400 |  |  |  | 2 | 6 | 13
[6 empty] | SPARE |  |  |  | DO | 24VDC |  | PW400 |  |  |  | 2 | 6 | 14
[6 empty] | SPARE |  |  |  | DO | 24VDC |  | PW400 |  |  |  | 2 | 6 | 15
Card Type: Digital OUT/ 16
TAG | [5 empty] | DESCRIPTION |  | LOCATION | JB No. | SIGNAL CATEGORY | SIGNAL TYPE | RELAY OUTPUT | POWER SUPPLY |  |  |  | RACK | SLOT | CHANNEL
XV-61111 | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | UCP-6101 | FIRLD | COMPRESSOR -A- SLIDE VALVE UNLOAD SOV |  | COMP SKID | JB-UEV-61112 | DO | 24VDC | WET CONTACT | PW400 | H |  | NIS | 2 | 7 | 0 | OFF | ON
XV-61112 | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | UCP-6101 | FIRLD | COMPRESSOR -A- SLIDE VALVE LOAD SOV |  | COMP SKID | JB-UEV-61112 | DO | 24VDC | WET CONTACT | PW400 | H |  | NIS | 2 | 7 | 1 | OFF | ON
XV-61121 | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | UCP-6101 | FIRLD | COMPRESSOR -B- SLIDE VALVE UNLOAD SOV |  | COMP SKID | JB-UEV-61122 | DO | 24VDC | WET CONTACT | PW400 | H |  | NIS | 2 | 7 | 2 | OFF | ON
XV-61122 | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | UCP-6101 | FIRLD | COMPRESSOR -B- SLIDE VALVE LOAD SOV |  | COMP SKID | JB-UEV-61122 | DO | 24VDC | WET CONTACT | PW400 | H |  | NIS | 2 | 7 | 3 | OFF | ON
XV-61151 | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | UCP-6101 | FIRLD | OIL RECOVERY VALVE SOV - COMPRESSOR DISCHARGE |  | VESSELS SKID | JB-UEV-61152 | DO | 24VDC | WET CONTACT | PW400 | H |  | NIS | 2 | 7 | 0 | OFF | ON
XV-61152 | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | UCP-6101 | FIRLD | OIL RECOVERY VALVE SOV - CHILLER RECOVERY |  | VESSELS SKID | JB-UEV-61152 | DO | 24VDC | WET CONTACT | PW400 | H |  | NIS | 2 | 7 | 1 | OFF | ON
[6 empty] | SPARE |  |  |  | DO | 24VDC |  | PW400 |  |  |  | 2 | 7 | 2
[6 empty] | SPARE |  |  |  | DO | 24VDC |  | PW400 |  |  |  | 2 | 7 | 3
[6 empty] | SPARE |  |  |  | DO | 24VDC |  | PW400 |  |  |  | 2 | 7 | 4
[6 empty] | SPARE |  |  |  | DO | 24VDC |  | PW400 |  |  |  | 2 | 7 | 5
XA-61101 | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | UCP-6101 | DCS | COMPRESSOR -A- TRIP COMPRESSOR |  | UCP-6101 | UCP-6101 | DO | 24VDC | DRY CONTACT | PW400 | H | S | NIS | 2 | 7 | 6 | OFF | ON
XA-61102 | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | UCP-6101 | DCS | COMMON -A- ALRM COMPRESSOR |  | UCP-6101 | UCP-6101 | DO | 24VDC | DRY CONTACT | PW400 | H | S | NIS | 2 | 7 | 7 | OFF | ON
XA-61103 | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | UCP-6101 | DCS | COMPRESSOR -B- TRIP COMPRESSOR |  | UCP-6101 | UCP-6101 | DO | 24VDC | DRY CONTACT | PW400 | H | S | NIS | 2 | 7 | 8 | OFF | ON
XA-61104 | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | UCP-6101 | DCS | COMMON -B- ALRM COMPRESSOR |  | UCP-6101 | UCP-6101 | DO | 24VDC | DRY CONTACT | PW400 | H | S | NIS | 2 | 7 | 9 | OFF | ON
UA-61199 | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | UCP-6101 | DCS | PLC FAULT |  | UCP-6101 | UCP-6101 | DO | 24VDC | DRY CONTACT | PW400 | H | S | NIS | 2 | 7 | 10 | OFF-PULSE | ON-PULSE
UA-61114 | Propylene | VD-GPIC-MA-3029-3029-0015 | BOOL | UCP-6101 | DCS | INTERLOCK ACTIVATED |  | UCP-6101 | UCP-6101 | DO | 24VDC | DRY CONTACT | PW400 | H | S | NIS | 2 | 7 | 11 | OFF-PULSE | ON-PULSE
STATES
TAG | SERVICE | PID DWG No. | TYPE | FROM | TO | DESCRIPTION | Engineering units | LOCATION | JB No. | SIGNAL CATEGORY | SIGNAL | RELAY OUTPUT | POWER SUPPLY | TYPE | SERIAL | IS/NIS | RACK | SLOT | CHANNEL | STATES'0' | STATES'1'
Card Type: Digital IN/ 16
Card Type/: Analog IN/ 8
TAG | [5 empty] | DESCRIPTION |  | LOCATION | JB No. | SIGNAL CATEGORY | SIGNAL TYPE | RELAY OUTPUT | POWER SUPPLY |  |  |  | RACK | SLOT | CHANNEL
PT-61111 | Propylene | VD-GPIC-MA-3029-3029-0015 | FLOAT/REAL | FIELD | UCP-6101 | COMPRESSOR -A- SUCTION PRESSURE | Bar | COMP SKID | JB-UIA-61111 | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 8 | 0
PT-61113 | Propylene | VD-GPIC-MA-3029-3029-0015 | FLOAT/REAL | FIELD | UCP-6101 | COMPRESSOR -A- OIL SUPPLY PRESSURE | Bar | COMP SKID | JB-UIA-61111 | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 8 | 1
TT-61111 | Propylene | VD-GPIC-MA-3029-3029-0015 | FLOAT/REAL | FIELD | UCP-6101 | COMPRESSOR -A-SUCTION TEMPERATURE | C | COMP SKID | JB-UIA-61111 | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 8 | 2
VT-61111 | Propylene | VD-GPIC-MA-3029-3029-0015 | FLOAT/REAL | FIELD | UCP-6101 | COMPRESSOR -A- CASING VIBRATION | G | COMP SKID | JB-UIA-61111 | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 8 | 3
ZT-61111 | Propylene | VD-GPIC-MA-3029-3029-0015 | FLOAT/REAL | FIELD | UCP-6101 | COMPRESSOR -A- SLIDE VALVE POSITION | % | COMP SKID | JB-UIA-61111 | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 8 | 4
[6 empty] | SPARE |  |  |  | AI | 4-20mA | - |  |  |  |  | 2 | 8 | 5
[6 empty] | SPARE |  |  |  | AI | 4-20mA | - |  |  |  |  | 2 | 8 | 6
[6 empty] | SPARE |  |  |  | AI | 4-20mA | - |  |  |  |  | 2 | 8 | 7
Card Type/: Analog IN/ 8
TAG | [5 empty] | DESCRIPTION |  | LOCATION | JB No. | SIGNAL CATEGORY | SIGNAL TYPE | RELAY OUTPUT | POWER SUPPLY |  |  |  | RACK | SLOT | CHANNEL
PT-61121 | Propylene | VD-GPIC-MA-3029-3029-0015 | FLOAT/REAL | FIELD | UCP-6101 | COMPRESSOR -B- SUCTION PRESSURE | Bar | COMP SKID | JB-UIA-61121 | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 9 | 0
PT-61123 | Propylene | VD-GPIC-MA-3029-3029-0015 | FLOAT/REAL | FIELD | UCP-6101 | COMPRESSOR -B- OIL SUPPLY PRESSURE | Bar | COMP SKID | JB-UIA-61121 | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 9 | 1
TT-61121 | Propylene | VD-GPIC-MA-3029-3029-0015 | FLOAT/REAL | FIELD | UCP-6101 | COMPRESSOR -B-SUCTION TEMPERATURE | C | COMP SKID | JB-UIA-61121 | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 9 | 2
VT-61121 | Propylene | VD-GPIC-MA-3029-3029-0015 | FLOAT/REAL | FIELD | UCP-6101 | COMPRESSOR -B- CASING VIBRATION | G | COMP SKID | JB-UIA-61121 | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 9 | 3
ZT-61121 | Propylene | VD-GPIC-MA-3029-3029-0015 | FLOAT/REAL | FIELD | UCP-6101 | COMPRESSOR -B- SLIDE VALVE POSITION | % | COMP SKID | JB-UIA-61121 | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 9 | 4
[6 empty] | SPARE |  |  |  | AI | 4-20mA | - |  |  |  |  | 2 | 9 | 5
[6 empty] | SPARE |  |  |  | AI | 4-20mA | - |  |  |  |  | 2 | 9 | 6
[6 empty] | SPARE |  |  |  | AI | 4-20mA | - |  |  |  |  | 2 | 9 | 7
Card Type/: Analog IN/ 8
TAG | [5 empty] | DESCRIPTION |  | LOCATION | JB No. | SIGNAL CATEGORY | SIGNAL TYPE | RELAY OUTPUT | POWER SUPPLY |  |  |  | RACK | SLOT | CHANNEL
PT-61131 | Propylene | VD-GPIC-MA-3029-3029-0015 | FLOAT/REAL | FIELD | UCP-6101 | COMMON DISCHARGE PRESSURE | Bar | COMP SKID | JB-UIA-61111 | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 10 | 0
PT-61132 | Propylene | VD-GPIC-MA-3029-3029-0015 | FLOAT/REAL | FIELD | UCP-6101 | COALESCER ELEMENT OUTLET PRESSURE | Bar | COMP SKID | JB-UIA-61111 | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 10 | 1
PT-61133 | Propylene | VD-GPIC-MA-3029-3029-0015 | FLOAT/REAL | FIELD | UCP-6101 | OIL FILTER SUPPLY PRESSURE | Bar | COMP SKID | JB-UIA-61111 | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 10 | 2
PT-61134 | Propylene | VD-GPIC-MA-3029-3029-0015 | FLOAT/REAL | FIELD | UCP-6101 | OIL SUPPLY PRESSURE | Bar | COMP SKID | JB-UIA-61111 | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 10 | 3
TT-61131 | Propylene | VD-GPIC-MA-3029-3029-0015 | FLOAT/REAL | FIELD | UCP-6101 | OIL SEPARATOR TEMPERATURE | C | COMP SKID | JB-UIA-61111 | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 10 | 4
TT-61132 | Propylene | VD-GPIC-MA-3029-3029-0015 | FLOAT/REAL | FIELD | UCP-6101 | OIL SUPPLY TEMPERATURE | C | COMP SKID | JB-UIA-61111 | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 10 | 5
LT-61131 | Propylene | VD-GPIC-MA-3029-3029-0015 | FLOAT/REAL | FIELD | UCP-6101 | OIL SEPARATOR LEVEL | % | COMP SKID | JB-UIA-61111 | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 10 | 6
[6 empty] | SPARE |  |  |  | AI | 4-20mA | - |  |  |  |  | 2 | 10 | 7
Card Type/: Analog IN/ 8
TAG | [5 empty] | DESCRIPTION |  | LOCATION | JB No. | SIGNAL CATEGORY | SIGNAL TYPE | RELAY OUTPUT | POWER SUPPLY |  |  |  | RACK | SLOT | CHANNEL
TIC-61101 | Propylene | VD-GPIC-MA-3029-3029-0014 | FLOAT/REAL | DCS | UCP-6100 | CHILLER TUBE OUTLET TEMPERTURE | C | VESSELS SKID | JB-UIA-61141 | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 11 | 0
LT-61151 | Propylene | VD-GPIC-MA-3029-3029-0015 | FLOAT/REAL | FIELD | UCP-6101 | CHILLER LEVEL | % | VESSELS SKID | JB-UIA-61141 | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 11 | 1
[6 empty] | SPARE |  |  |  | AI | 4-20mA | - | PW400 |  |  |  | 2 | 11 | 2
PT-61141 | Propylene | VD-GPIC-MA-3029-3029-0015 | FLOAT/REAL | FIELD | UCP-6101 | ECONOMIZER TUBESIDE PRESSURE | Bar | COMP SKID | JB-UIA-61141 | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 11 | 3
TT-61141 | Propylene | VD-GPIC-MA-3029-3029-0016 | FLOAT/REAL | FIELD | UCP-6101 | ECONOMIZER TUBESIDE TEMPERATURE | Bar | COMP SKID | JB-UIA-61141 | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 11 | 4
TT-61190 | Propylene | VD-GPIC-MA-3029-3029-0015 | FLOAT/REAL | UCP-6101 | UCP-6101 | UNIT CONTROL PANEL TEMPERATURE | C | UCP-6101 | UCP-6101 | AI | 4-20mA | - | PW400 | H | S | NIS | 2 | 11 | 5
[6 empty] | SPARE |  |  |  | AI | 4-20mA |  | PW400 |  |  |  | 2 | 11 | 6
[6 empty] | SPARE |  |  |  | AI | 4-20mA |  | PW400 |  |  |  | 2 | 11 | 7
Card Type/: Analog IN/ 8
TAG | [5 empty] | DESCRIPTION |  | LOCATION | JB No. | SIGNAL CATEGORY | SIGNAL TYPE | RELAY OUTPUT | POWER SUPPLY |  |  |  | RACK | SLOT | CHANNEL
TE-61117 | Propylene | VD-GPIC-MA-3029-3029-0015 | FLOAT/REAL | FIELD | UCP-6101 | COMPRESSOR MOTOR -A- BEARING TEMP DE | C | COMP -A- SKID | MOTOR JB | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 12 | 0
TE-61118 | Propylene | VD-GPIC-MA-3029-3029-0015 | FLOAT/REAL | FIELD | UCP-6101 | COMPRESSOR MOTOR -A- BEARING TEMP NDE | C | COMP -A- SKID | MOTOR JB | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 12 | 1
TE-61127 | Propylene | VD-GPIC-MA-3029-3029-0015 | FLOAT/REAL | FIELD | UCP-6101 | COMPRESSOR MOTOR -B- BEARING TEMP DE | C | COMP -B- SKID | MOTOR JB | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 12 | 2
TE-61128 | Propylene | VD-GPIC-MA-3029-3029-0015 | FLOAT/REAL | FIELD | UCP-6101 | COMPRESSOR MOTOR -B- BEARING TEMP NDE | C | COMP -B- SKID | MOTOR JB | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 12 | 3
[6 empty] | SPARE |  |  |  | AI | 4-20mA |  | PW400 |  |  |  | 2 | 12 | 4
[6 empty] | SPARE |  |  |  | AI | 4-20mA |  | PW400 |  |  |  | 2 | 12 | 5
IT-61111 | Propylene | VD-GPIC-MA-3029-3029-0015 | FLOAT/REAL | MCC | UCP-6101 | COMPRESSOR -A- MOTOR CURRENT | AMPS | MCC | UCP-6101 | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 12 | 6
IT-61121 | Propylene | VD-GPIC-MA-3029-3029-0016 | FLOAT/REAL | MCC | UCP-6102 | COMPRESSOR -B- MOTOR CURRENT | AMPS | MCC | UCP-6102 | AI | 4-20mA | - | PW400 | H | S | IS | 2 | 12 | 7
Card Type: Analog OUT 4
TAG | [5 empty] | DESCRIPTION |  | LOCATION | JB No. | SIGNAL CATEGORY | SIGNAL TYPE | RELAY OUTPUT | POWER SUPPLY |  |  |  | RACK | SLOT | CHANNEL
PYI-61151 | Propylene | VD-GPIC-MA-3029-3029-0015 | FLOAT/REAL | UCP-6101 | FIELD | HOT GAS BYPASS CONTROL VALVE | % | VESSELS SKID | JB-UIA-61141 | AO | 4-20 mA | - | - | H | S | IS | 2 | 13 | 0
LYI-61151 | Propylene | VD-GPIC-MA-3029-3029-0015 | FLOAT/REAL | UCP-6101 | FIELD | CHILLER LEVEL CONTROL VALVE | % | VESSELS SKID | JB-UIA-61141 | AO | 4-20 mA | - | - | H | S | IS | 2 | 13 | 1
TPYI-61141 | Propylene | VD-GPIC-MA-3029-3029-0016 | FLOAT/REAL | UCP-6102 | FIELD | ECONOMIZER TEMPERATURE CONTROL VALVE | % | VESSELS SKID | JB-UIA-61141 | AO | 4-20 mA | - | - | H | S | IS | 2 | 13 | 2
[6 empty] | SPARE |  |  |  | AO | 4-20 mA |  | - |  |  |  | 2 | 13 | 3