## Unit A-B
COMPRESSOR C-6101A/B
No. | Service | Tag No. | Content of signal | SIGNAL Type | IS/NIS | Cable type | Cable size | Gland size | Cable Tag. | From | To | Length Meter(+20% spare) | Remarks
1 | Compressor A Suction pressure transmitter | PT-61111 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20 | PT-61111 | PT-61111 | JB-UIA-611 | 10
2 | Common Discharge pressure transmitter | PT-61131 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20 | PT-61131 | PT-61131 | JB-UIA-611 | 10
3 | Oil Supply- Compressor A pressure transmitter | PT-61113 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20 | PT-61113 | PT-61113 | JB-UIA-611 | 10
4 | Upstream oil filter pressure transmitter | PT-61133 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20 | PT-61133 | PT-61133 | JB-UIA-611 | 10
5 | Coalescer Element Outlet pressure transmitter | PT-61132 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20 | PT-61132 | PT-61132 | JB-UIA-611 | 10
6 | Downstream oil filter pressure transmitter | PT-61134 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20 | PT-61134 | PT-61134 | JB-UIA-611 | 10
7 | Compressor A Suction temperature transmitter | TT-61111 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20 | TT-61111 | TT-61111 | JB-UIA-611 | 10
8 | Oil Separator temperature transmitter | TT-61131 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20 | TT-61131 | TT-61131 | JB-UIA-611 | 10
9 | Oil header compressor temperature transmitter | TT-61132 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20 | TT-61132 | TT-61132 | JB-UIA-611 | 10
10 | Oil Separator level transmitter | LT-61131 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20 | LT-61131 | LT-61131 | JB-UIA-611 | 10
11 | Compressor A slide valve position sensor | ZE-61111 | 3-wire | Analouge | IS | (CU/XLPE/PVC/SWA/PVC) Blue | 01Tx1.5mm² | M20 | ZE-61111 | ZE-61111 | JB-UIA-611 | 10
12 | Multi cable for JB-UIA-611 | IC-UIA-611 | 4 to 20mA | Analouge | IS | FRT-19Px1mm² SCR/OSCR/SWA/IS/BLUE (300/500) | 19x2x1 mm² | M40 | IC-UIA-611 | JB-UIA-611 | UCP-6101 | 350 | 1-Cable will be supplied By Customer
13 | Compressor B Suction pressure transmitter | PT-61121 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20 | PT-61121 | PT-61121 | JB-UIA-621 | 10
14 | Oil Supply- Compressor B pressure transmitter | PT-61123 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20 | PT-61123 | PT-61123 | JB-UIA-621 | 10
15 | Compressor B Suction temperature transmitter | TT-61121 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20 | TT-61121 | TT-61121 | JB-UIA-621 | 10
16 | Compressor B slide valve position sensor | ZE-61121 | 3-wire | Analouge | IS | (CU/XLPE/PVC/SWA/PVC) Blue | 01Tx1.5mm² | M20 | ZE-61121 | ZE-61121 | JB-UIA-621 | 10
17 | Multi cable for JB-UIA-621 | IC-UIA-621 | 4 to 20mA | Analouge | IS | FRT-07Px1mm² SCR/OSCR/SWA/IS/BLUE (300/500) | 7x2x1 mm² | M25 | IC-UIA-621 | JB-UIA-621 | UCP-6101 | 350 | 1-Cable will be supplied By Customer
18 | ECONOMIZER TUBESIDE TEMPERATURE | TT-61141 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20 | TT-61141 | TT-61141 | JB-UIA-641 | 10
19 | ECONOMIZER TUBESIDE PRESSURE | PT-61141 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20 | PT-61141 | PT-61141 | JB-UIA-641 | 10
20 | Chiller level transmitter | LT-61151 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20 | LT-61151 | LT-61151 | JB-UIA-641 | 10
21 | Chiller level control valve | LV-61151 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20 | LV-61151 | LV-61151 | JB-UIA-641 | 10
22 | Hot Gas Bypass control valve | PV-61151 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20 | PV-61151 | PV-61151 | JB-UIA-641 | 10
23 | ECONOMIZER TEMPERATURE CONTROL VALVE | TV-61141 | 4 to 20mA / 2-wire | Analouge | IS | Type 1 | 01Px1.5mm² | M20 | TV-61141 | TV-61141 | JB-UIA-641 | 10
24 | Multi cable for JB-UIA-641 | IC-UIA-641 | 4 to 20mA | Analouge | IS | FRT-07Px1mm² SCR/OSCR/SWA/IS/BLUE (300/500) | 7x2x1 mm² | M25 | IC-UIA-641 | JB-UIA-641 | UCP-6101 | 350 | 1-Cable will be supplied By Customer
25 | COMPRESSOR -A- SLIDE VALVE 100% | ZSH-61111 | 24Vdc / **W | Digital | IS
26 | COMPRESSOR -A- SLIDE VALVE 0% | ZSL-61111 | 24Vdc / **W | Digital | IS
27 | Multi cable for ZS-61111 | ZS-61111 | 24Vdc / **W | Digital | IS | FRT-02Px1.5mm² OSCR/SWA/IS/BLUE (300/500) | 2x2x1.5 mm² | By Client | IC-ZS-61111 | A-Slide valve Potentiometer switch | UCP-6101 | 350 | 1-Cable will be supplied By Customer
28 | COMPRESSOR -B- SLIDE VALVE 100% | ZSH-61121 | 24Vdc / **W | Digital | IS
29 | COMPRESSOR -B- SLIDE VALVE 0% | ZSL-61121 | 24Vdc / **W | Digital | IS
30 | Multi cable for ZS-61121 | ZS-61121 | 24Vdc / **W | Digital | IS | FRT-02Px1.5mm² OSCR/SWA/IS/BLUE (300/500) | 2x2x1.5 mm² | By Client | IC-ZS-61121 | B-Slide valve Potentiometer switch | UCP-6101 | 350 | 1-Cable will be supplied By Customer
31 | COMPRESSOR -A- SLIDE VALVE UNLOAD SOV | XY-61111 | 24Vdc / **W | Digital | NIS | Type 2 | 01Px2.5mm² | M20 | XY-61111 | XY-61111 | JB-UEV-612 | 10
32 | COMPRESSOR -A- SLIDE VALVE LOAD SOV | XY-61112 | 24Vdc / **W | Digital | NIS | Type 2 | 01Px2.5mm² | M20 | XY-61112 | XY-61112 | JB-UEV-612 | 10
33 | Multi cable for JB-UEV-612 | IC-UEV-612 | 24Vdc / **W | Digital | NIS | FRT-04Px2.5mm² SWA/NIS/GRAY (300/500) | 4x2x2.5 mm² | M32 | IC-UEV-612 | JB-UEV-612 | UCP-6101 | 350 | 1-Cable will be supplied By Customer
34 | COMPRESSOR -B- SLIDE VALVE UNLOAD SOV | XY-61121 | 24Vdc / **W | Digital | NIS | Type 2 | 01Px2.5mm² | M20 | XY-61121 | XY-61121 | JB-UEV-622 | 10
35 | COMPRESSOR -B- SLIDE VALVE LOAD SOV | XY-61122 | 24Vdc / **W | Digital | NIS | Type 2 | 01Px2.5mm² | M20 | XY-61122 | XY-61122 | JB-UEV-622 | 10
36 | Multi cable for JB-UEV-622 | IC-UEV-622 | 24Vdc / **W | Digital | NIS | FRT-04Px2.5mm² SWA/NIS/GRAY (300/500) | 4x2x2.5 mm² | M32 | IC-UEV-622 | JB-UEV-622 | UCP-6101 | 350 | 1-Cable will be supplied By Customer
37 | OIL RECOVERY VALVE SOV - COMPRESSOR DISCHARGE | XY-61151 | 24Vdc / **W | Digital | NIS | Type 2 | 01Px2.5mm² | M20 | XY-61151 | XY-61151 | JB-UEV-652 | 10
38 | OIL RECOVERY VALVE SOV - CHILLER RECOVERY | XY-61152 | 24Vdc / **W | Digital | NIS | Type 2 | 01Px2.5mm² | M20 | XY-61152 | XY-61152 | JB-UEV-652 | 10
39 | Multi cable for JB-UEV-652 | IC-UEV-652 | 24Vdc / **W | Digital | NIS | FRT-04Px2.5mm² SWA/NIS/GRAY (300/500) | 4x2x2.5 mm² | M32 | IC-UEV-652 | JB-UEV-652 | UCP-6101 | 350 | 1-Cable will be supplied By Customer
40 | Oil heater temp. control switch High/High High | TSH-EH6101/TSHH-EH6101 | 24Vdc / **D | Digital | NIS | FRT-01Px1.5mm² OSCR/SWA/NIS/GRAY (300/500) | 1x2x1.5mm² | M20 | TS-EH6101 | TS-EH6101 | MCC | 350 | 1-Cable will be supplied by Electrical of Customer.
41 | COMPRESSOR -A- MOTOR CURRENT | IT-61111 | 4 to 20mA / 2-wire | Analouge | NIS | By Client | 2Px1.5mm² /Pr. 1 | M20 | IT-UCP6101 | MCC | UCP-6101 |  | 1-Cable will be supplied by Electrical of Customer.
42 | COMPRESSOR -B- MOTOR CURRENT | IT-61121 | 4 to 20mA / 2-wire | Analouge | NIS | By Client | 2Px1.5mm²/Pr. 2 | M20 | IT-UCP6101 | MCC | UCP-6101 | 350 | 1-Cable will be supplied by Electrical of Customer.
44 | COMPRESSOR MOTOR -B- BEARING TEMP NDE/DE | TE-61127/28 | RTD / 3 wire | Pt100 | IS | FRT-04Tx1mm² SCR/OSCR/SWA/IS (300/500) | 4Tx1 mm² | M32 | UCP-RTDBOX-B | Motor JB-B | UCP-6101 | 350 | 1-Cable will be supplied By Customer
46 | COMPRESSOR MOTOR -A- BEARING TEMP NDE/DE | TE-61117/18 | RTD / 3 wire | Pt100 | IS | FRT-04Tx1mm² SCR/OSCR/SWA/IS (300/500) | 4Tx1 mm² | M32 | UCP-RTDBOX-A | Motor JB-A | UCP-6101 | 350 | 1-Cable will be supplied By Customer
47 | CHILLER TUBE OUTLET TEMPERTURE | TIC-61101 | 4 to 20mA / 2-wire | Analouge | IS | FRT-01Px1.5mm² OSCR/IS/BLUE (300/500) | 1Px1.5mm² | M20 | TIC-61101 | DCS | UCP-6101 | 50 | 1-Cable will be supplied By Customer
50 | Plant Emergency Stop | ESD-61010 | 24Vdc / **D | Digital | NIS | FRT-01Px1.5mm² OSCR/NIS/GRAY (300/500) | 1Px1.5mm² | M20 | ESD-61010 | ESD | UCP-6101 | 50 | 1-Cable will be supplied By Customer
51 | CUMULATIVE ALARM | XA-61101 | 24Vdc / **D | Digital | NIS | FRT-01Px1.5mm² OSCR/NIS/GRAY (300/500) | 1Px1.5mm² | M20 | UCP-DCS | UCP-6101 | DCS | 50 | 1-Cable will be supplied By Customer
52 | CUMULATIVE TRIP | XA-61102 | 24Vdc / **D | Digital | NIS | FRT-01Px1.5mm² OSCR/NIS/GRAY (300/500) | 1Px1.5mm² | M20 | UCP-DCS | UCP-6101 | DCS | 50 | 1-Cable will be supplied By Customer
53 | Time Synchronization Signal | TS‐6101 | 24Vdc / **D | Digital | NIS | FRT-01Px1.5mm² OSCR/NIS/GRAY (300/500) | 1Px1.5mm² | M20 | UCP-DCS | DCS | UCP-6101 | 50 | 1-Cable will be supplied By Customer
54 | LCP-A- Switches | UCP-LCP-6101A-1 | 24Vdc / **D | Digital | NIS | FRT-19Px1mm² OSCR/SWA/NIS/GRAY (300/500) | 19Px1 mm² | M32 | UCP-LCP-6101A-1 | LCP-6101A | UCP-6101 | 350 | 1-Cable will be supplied By Customer
55 | LCP -A-Lamps | UCP-LCP-6101A-2 | 24Vdc / **D | Digital | NIS | FRT-07Px2.5mm² SWA/NIS/GRAY(300/500) | 7Px2.5 mm² | M32 | UCP-LCP-6101A-2 | LCP-6101A | UCP-6101 | 350 | 1-Cable will be supplied By Customer
56 | LCP-B- Switches | UCP-LCP-6101B-1 | 24Vdc / **D | Digital | NIS | FRT-07Px1mm² SWA/NIS/GRAY(300/500) | 7Px1 mm² | M25 | UCP-LCP-6101B-1 | LCP-6101B | UCP-6101 | 350 | 1-Cable will be supplied By Customer
57 | LCP -B-Lamps | UCP-LCP-6101B-2 | 24Vdc / **D | Digital | NIS | FRT-04Px2.5mm² SWA/NIS/GRAY(300/500) | 4Px2.5 mm² | M32 | UCP-LCP-6101B-2 | LCP-6101B | UCP-6101 | 350 | 1-Cable will be supplied By Customer
58 | UCP to MCC (UCP Digital Output Command signals for main motor A, main motor B, oil pump, Elec. Heater :STT,STP, ETC) |  | 24Vdc / **D | Digital | NIS | By Client | 12x2x2.5 mm² | By Client | Hold | UCP-6101 | MCC | 350 | Cable will be supplied by Electrical of Customer.
59 | MCC to UCP (UCP Digital Input Status signals for main motor A, main motor B, oil pump, Elec. Heater : Running,Fault, ETC) |  | 24Vdc / **D | Digital | NIS | By Client | 12x2x2.5 mm² | By Client | Hold | MCC | UCP-6101 | 350 | Cable will be supplied by Electrical of Customer.
60 | Communication with DCS |  |  | Modbus TCP/IP |  | By Client |  |  | DCS-UCP-6101-1 | UCP | DCS | 50
61 | Communication with DCS |  |  | Modbus TCP/IP |  | By Client |  |  | DCS-UCP-6101-2 | UCP | DCS | 50 | Redundant
62 | UPS Power_110 Vac -#1 |  |  | Power cable |  | CU/XLPE/PVC (600/1000) Black | 02Cx6mm2 |  | PDP-UCP-6101-1 | Instrument PDP | UCP | 50 | 1-Cable will be supplied By Customer
63 | UPS Power_110 Vac -#2 |  |  | Power cable |  | CU/XLPE/PVC (600/1000) Black | 02Cx6mm2 |  | PDP-UCP-6101-2 | Instrument PDP | UCP | 50
64 | Non-UPS Power |  |  | Power cable |  | CU/XLPE/PVC (600/1000) Black | 02Cx4mm2 |  | PDP-UCP-6101-3 | Instrument PDP | UCP | 50

## Type1
Rev.
1 | Item | 1
2 | DUTY | 2 Wire Transmitter,
3 | INSTALLATION LOCATION | OUTDOOR
4 | INSTALLATION METHOD | -
5 | AMBIENT TEMP MIN / MAX | -20 °C / 48 °C
6 | CABLE TECHNICAL DATA
7 | MAKE | Moghan Cable
8 | TYPE | As per EN50288-7
9 | CONDUCTORS | Tinned Stranded Copper - IEC 60228 class 2
10 | INSULATION | XLPE
11 | CORE / PAIR / TRIAD | Twisted Pair
12 | IDENTIFICATION | Black - white
13 | SCREENING | Collective Aluminium/Polyester tape + tinned copper drain wire
14 | BEDDING | LSHF
15 | ARMOUR | Galvanised Steel Wire Armour (SWA)
16 | OUTER JACKET | LSHF
17 | OUTER SHEATH COLOUR | Blue
18 | CROSS SECTION | 1.5 mm2
19 | NUMBER OF CORES / PARE / TRIADS | 1 Pair
20 | MAX. OPERATING VOLTAGE | 300 / 500 Volt
21 | MIN. OPERATING TEMPERATURE | -20 °C
22 | MAX. OPERATING TEMPERATURE | +60 °C
23 | CONDUCTOR MAXIMUM TEMPERATURE | +90 °C
24
25 | INNER SHEATH DIAMETER | 7.7 mm
26 | OUTER SHEATH DIAMETER | 12.5 mm
27
28 | FLAME RETARDANT | IEC60332-1-2 / IEC 60332-3-24 (cat.C)
29
30
31
32
33
34
35

## Type2
Rev.
1 | Item | 2
2 | DUTY | SOLENOID VALVE
3 | INSTALLATION LOCATION | OUTDOOR
4 | INSTALLATION METHOD | -
5 | AMBIENT TEMP MIN / MAX | -20 °C / 48 °C
6 | CABLE TECHNICAL DATA
7 | MAKE | Moghan Cable
8 | TYPE | As per EN50288-7
9 | CONDUCTORS | Tinned Stranded Copper - IEC 60228 class 2
10 | INSULATION | XLPE
11 | CORE / PAIR / TRIAD | Pair
12 | IDENTIFICATION | Black - white
13 | SCREENING | NA
14 | BEDDING | LSHF
15 | ARMOUR | Galvanised Steel Wire Armour (SWA)
16 | OUTER JACKET | LSHF
17 | OUTER SHEATH COLOUR | Gray
18 | CROSS SECTION | 2.5 mm2
19 | NUMBER OF CORES / PARE / TRIADS | 1 Pair
20 | MAX. OPERATING VOLTAGE | 300 / 500 Volt
21 | MIN. OPERATING TEMPERATURE | -20 °C
22 | MAX. OPERATING TEMPERATURE | +60 °C
23 | CONDUCTOR MAXIMUM TEMPERATURE | +90 °C
24
25 | INNER SHEATH DIAMETER | 8.9 mm
26 | OUTER SHEATH DIAMETER | 13.7 mm
27
28 | FLAME RETARDANT | IEC60332-1-2 / IEC 60332-3-24 (cat.C)
29
30
31
32
33
34
35

## Type3
Rev.
1 | Item | 3
2 | DUTY | Switches
3 | INSTALLATION LOCATION | OUTDOOR
4 | INSTALLATION METHOD | -
5 | AMBIENT TEMP MIN / MAX | -20 °C / 48 °C
6 | CABLE TECHNICAL DATA
7 | MAKE | AVL
8 | TYPE | As per EN50288-7
9 | CONDUCTORS | Stranded Copper - IEC 60228 class 2
10 | INSULATION | XLPE
11 | CORE / PAIR / TRIAD | Twisted Pair
12 | IDENTIFICATION | Black - white
13 | SCREENING | Collective Aluminium/Maylar tape + tinned copper drain wire
14 | BEDDING | PVC
15 | ARMOUR | Galvanised Steel Wire Armour (SWA)
16 | OUTER JACKET | PVC
17 | OUTER SHEATH COLOUR | Blue
18 | CROSS SECTION | 1.5 mm2
19 | NUMBER OF CORES / PARE / TRIADS | 2 Pair
20 | MAX. OPERATING VOLTAGE | 300 / 500 Volt
21 | MIN. OPERATING TEMPERATURE | -20 °C
22 | MAX. OPERATING TEMPERATURE | +60 °C
23 | CONDUCTOR MAXIMUM TEMPERATURE | +90 °C
24
25 | INNER SHEATH DIAMETER | Later
26 | OUTER SHEATH DIAMETER | Later
27
28 | FLAME RETARDANT | IEC60332-1-2 / IEC 60332-3-24 (cat.C)
29
30
31
32
33
34
35