## Resolution Sheet
|  |  |  | PROJECT: | Integrated Methanol and Ammonia Plant
COMMENT RESOLUTION SHEET FOR: |  |  |  |  | DOC TITLE: | DOC No:
[5 empty] | Wiring Diagram | N-278-VD-6019-IN-DIA-0005-01
Item no. | Page | Revision | Status | Client Comments | AirPack's Reply #1 | Client Reply #1 | AirPack's Reply #2 | Client Reply #2
1 | 1 | 01 |  | - This document should be submitted after finalizing P&ID, I/O List and Outline Dimensional Drawings documents . - Plz find other comment in next pages. | - Document submitted as per VDS. - Noted. | Will be checked again after finalizing PID, Compatibility with other vendor documents including PID, IO List, Outline Dimensional Drawings, ...is vendor responsibility and scope.
2 | 6 | 01 |  | As per project specification, Tag LCP should be modified to "300LP-820" | Tag correct as per P&ID. If tag is not correct according to project specification, please make comment in the P&ID first, tag will then be updated in the wiring diagram and all other subsequent documentation. | Noted. It is commented in last PID
3 | 6 | 01 |  | symbol and legend should be added. | Added symbol legend. | Noted.
4 | 7 | 01 |  | - Cable for all digital signals should be multi core - Tag cable : will be checked after finalizing data sheet document , (IS or NIS instrument should be determined in data sheet document) | - Cable changed to multicore cable. - It has already been determined that all instruments are non Ex instruments (installed in safe area) and are NIS. - If tag cable is not correct, please provide correct cable tag in order to avoid confusion and reduce project delays. | -Noted -Noted -It is mentioned in new comment
5 | 7 | 01 |  | terminal tag should be follow spec of project | Terminal tags updated, if terminal tags are not correct, please provide correct tag in order to avoid confusion and reduce project delays. | -It is mentioned in new comment
6 | 7 | 01 |  | As project spec : Following colors shall be used for identification:  Single and multi core: Black types of instrumentation cables :  Analogue cables (multi & single pair)  Digital cables (multi & single core) | Updated as per porject spec. | -It is mentioned in new comment
7 | 7 | 01 |  | from MCC following signals will be sent to LCP via free voltage contact: 1- run 2- fault 3- available vendor to consider them inside LCP | According to P&ID, there will be no MCC signals in the LCP. The LCP only has lamps and buttons. The entire package is controlled by the DCS of the customer. | signals means the contact for the signal lamps.run , fault , available will send to lcp for operating the signal lamps |  |  | Open
8 | 13 | 01 |  | As per project specification, Tag JB(LCP) and tag cable should be modified. For NIS signal Analog : 300JDAN-820/300CDAN-820 For IS signal Analog : 300JDAI-820 (If any) | Cable tag updated. Junction box tag kept the same as the tag on the P&ID for reasons mentioned earlier. All signals NIS. | Refer to Item 2
9 | 13 | 01 |  | Should be Modified .(19x2x0.75) | Updated. | Noted
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32