## Resolution Sheet
|  |  |  | PROJECT: | Integrated Methanol and Ammonia Plant
COMMENT RESOLUTION SHEET FOR: |  |  |  |  | DOC TITLE: | DOC No:
[5 empty] | Wiring Diagram | N-278-VD-6019-IN-DIA-0005-01
Item no. | Page | Revision | Status | Client Comments | AirPack's Reply #1 | Client Reply #1 | AirPack's Reply #2 | Client Reply #2
1 | 1 | 01 |  | - This document should be submitted after finalizing P&ID, I/O List and Outline Dimensional Drawings documents . - Plz find other comment in next pages. | - Document submitted as per VDS. - Noted. | Will be checked again after finalizing PID, Compatibility with other vendor documents including PID, IO List, Outline Dimensional Drawings, ...is vendor responsibility and scope. | Noted.
2 | 6 | 01 |  | As per project specification, Tag LCP should be modified to "300LP-820" | Tag correct as per P&ID. If tag is not correct according to project specification, please make comment in the P&ID first, tag will then be updated in the wiring diagram and all other subsequent documentation. | Noted. It is commented in last PID | Noted.
3 | 6 | 01 |  | symbol and legend should be added. | Added symbol legend. | Noted.
4 | 7 | 01 |  | - Cable for all digital signals should be multi core - Tag cable : will be checked after finalizing data sheet document , (IS or NIS instrument should be determined in data sheet document) | - Cable changed to multicore cable. - It has already been determined that all instruments are non Ex instruments (installed in safe area) and are NIS. - If tag cable is not correct, please provide correct cable tag in order to avoid confusion and reduce project delays. | -Noted -Noted -It is mentioned in new comment | Noted.
5 | 7 | 01 |  | terminal tag should be follow spec of project | Terminal tags updated, if terminal tags are not correct, please provide correct tag in order to avoid confusion and reduce project delays. | -It is mentioned in new comment | Noted.
6 | 7 | 01 |  | As project spec : Following colors shall be used for identification:  Single and multi core: Black types of instrumentation cables :  Analogue cables (multi & single pair)  Digital cables (multi & single core) | Updated as per porject spec. | -It is mentioned in new comment | Noted.
7 | 7 | 01 |  | from MCC following signals will be sent to LCP via free voltage contact: 1- run 2- fault 3- available vendor to consider them inside LCP | According to P&ID, there will be no MCC signals in the LCP. The LCP only has lamps and buttons. The entire package is controlled by the DCS of the customer. | signals means the contact for the signal lamps.run , fault , available will send to lcp for operating the signal lamps | Comment unclear, if lamp signals are not correct, please comment on the P&ID and the control philosophy. The wiring diagram will then be updated accordingly. | all signal lamps will be connected to control system , MCC will send the datas to control system | Open
8 | 13 | 01 |  | As per project specification, Tag JB(LCP) and tag cable should be modified. For NIS signal Analog : 300JDAN-820/300CDAN-820 For IS signal Analog : 300JDAI-820 (If any) | Cable tag updated. Junction box tag kept the same as the tag on the P&ID for reasons mentioned earlier. All signals NIS. | Refer to Item 2 | Noted.
9 | 13 | 01 |  | Should be Modified .(19x2x0.75) | Updated. | Noted
10 | 4 | 02 |  | with | Updated.
11 | 4 | 02 |  | hot dipp galvanized | Updated.
12 | 7 | 02 |  | RE-comment: As per project specification, Tag LCP should be modified to "300LP-820" | Updated.
13 | 7 | 02 |  | General Note: General Comment: 1- Any changes in next revision to be marked with revision mark. 2- If any comments is not applicable please send reply sheet. 3- Compatibility with project requirement is vendor responsibility and scope, and next comments are just for hint. 4- Compatibility with other vendor documents including PID, IO List, Outline Dimensional Drawings, ...is vendor responsibility and scope. 5- This document will be checked again after finalizing PID document. 6- all Tag name in all documents should be same format. no needs "-" after prefix 320. example correct format is 320TT-8201, ... . | 1 - It is not possible to mark revisions changes in Eplan. 2 - CRS is always sent, as above. 3 - You're package will be manufactured according to the approved project documents. 4 - Noted. Every effort is made to ensure all project documents are aligned. 5 - Noted. 6 - Updated. | 1 - clarify !!!! In all revision eplan software from Eplan 5.5 to P8 electrical or propanel , you can mention revision mark. For The easiest way, plz refer to PDF file. 2- Noted 3 - Contractor's comments do not relieve, in any case, Vendor from their responsibilities. 4 - Noted 5 - Noted 6 - Noted
14 | 7 | 02 |  | 300TDD820 | Updated. | Noted
15 | 7 | 02 |  | 300TED820 | Updated. | Noted
16 | 8 | 02 |  | Local/Remote - should be checked and clarify. one signal is considered in IO list document for local /Remote. | Updated. | Noted
17 | 8 | 02 |  | Clarify why off position is used ? | Updated to two position switch without off position. | Noted
18 | 8 | 02 |  | Incompatible with legend, two or three position? | Updated to two position, legend also updated. | Noted
19 | 8 | 02 |  | As project spec : Following colors shall be used for identification:  Single and multi core: Black types of instrumentation cables :  Analogue cables (multi & single pair)  Digital cables (multi & single core) | Noted. | Single and multi core: Black for all digital signal. Emergency push button is missed. Plz modify
20 | 8 | 02 |  | 1 BK | Updated. | Noted
21 | 8 | 02 |  | 2 BK | Updated. | Noted
22 | 8 | 02 |  | 3 BK | Updated. | Noted
23 | 8 | 02 |  | 4 BK | Updated. | Noted
24 | 8 | 02 |  | 20Cx1.5 mm2 | Updated. | Noted
25 | 8 | 02 |  | 300CDDN820 | Updated. | Noted
26 | 8 | 02 |  | 300TDD820 | Updated. | Noted
27 | 8 | 02 |  | All Tags should be modified(refer to general note) | Updated. | Noted
28 | 9 | 02 |  | these two signals are combined in MCC as fault | Lamp signals correct according to P&ID, if signals are not correct, please comment on the P&ID first.
29 | 9 | 02 |  | we do not have such a signal in MCC , only run , fault and available can be sent to package | Lamp signals correct according to P&ID, if signals are not correct, please comment on the P&ID first.
30 | 10 | 02 |  | 300TED820 | Updated. | Noted
31 | 10 | 02 |  | 300CED820 | Updated. | Noted
32 | 13 | 02 |  | 300TDA820 | Updated. | Noted
33 | 13 | 02 |  | 300TDA821 | Updated. | Noted
34 | 14 | 02 |  | 300CDAN820 | Updated. | Noted
35 | 14 | 02 |  | 300TDA820 | Updated. | Noted
36 | 14 | 02 |  | 320PT-8201 | Updated. | Noted
37 | 14 | 02 |  | should be modified (refer to general note) | Updated. | Noted
38 | 18 | 02 |  | 300TDA821 | Updated. | Noted
39 | 1 | 03 |  | - This document should be revised after the finalization PID and IO list document if needed. - Please issue the next Rev. after the finalization PID and IO List document - Lamp test Push button should be added, as per TCL, this comment should be implemented in PID document too. | Updated as per the latest P&ID. | As per TCL, Lamp test push button should be considered in LPS, then should be added in wiring diagram and other related document(Outline Dimensional Drawings and IO List) and As per reply sheet next The P&ID should be updated and shared throughout The project when something changed.
40 | 9 | 03 |  | this signal is feeder available in MCC. which means feeder is not faulty and also mccb is not withdrawn | Updated as per the latest P&ID. | Noted
41 | 9 | 03 |  | there is just one fault signal from MCC to package | Updated as per the latest P&ID. | Noted
42 | 10 | 03 |  | Re commentAs project spec : Following colors shall be used for identification:  Single and multi core: Black | Updated. | Noted
43 | 10 | 03 |  | 1BK | Updated. | Noted
44 | 10 | 03 |  | 2BK | Updated. | Noted
45 | 10 | 03 |  | 3BK | Updated. | Noted
46 | 10 | 03 |  | 4BK | Updated. | Noted
47
48
49
50
51
52