## Resolution Sheet
|  |  |  | PROJECT: | Integrated Methanol and Ammonia Plant
COMMENT RESOLUTION SHEET FOR: |  |  |  |  | DOC TITLE: | DOC No:
[5 empty] | Outline Dimensional Drawings for LCP Panel and Junction Box | N-278-VD-6019-IN-DWG-0007-01
Item no. | Page | Revision | Status | Client Comments | AirPack's Reply #1 | Client Reply #1 | AirPack's Reply #2 | Client Reply #2
1 | 4 | 01 |  | Terminal stripe tag should be mentioned | Updated. | Noted
2 | 4 | 01 |  | All Tags should be revised as per comments of wiring Diagram document. | Updated. | Noted
3 | 4 | 01 |  | General Note: General Comment: 1- Any changes in next revision to be marked with revision mark. 2- If any comments is not applicable please send reply sheet. 3- Compatibility with other vendor documents including PID, IO List, Outline Dimensional Drawings, ...is vendor responsibility and scope. 4- This document will be checked again after finalizing PID document. | 1 - Revision markers added. 2 - CRS is always sent. 3 - Noted. 4 - Noted. | Noted
4 | 4 | 01 |  | Color, Thickness, Material should be added | Color added. Thickness added. Material already mentioned. | Noted
5 | 4 | 01 |  | comments should be implemented for Junction box Too. | Comments inorporated on junction box as well. | Noted
6 | 4 | 01 |  | if it is for push bottom and lamps M32 is enough | Updated.
Open
7 |  | 02 | 3 | Should be according to latest sub vendor list document | All components will be according to sub vendor list.
8 |  | 02 | 3 | cable gland and Gap should be added to the list | Comment unclear, what is meant by Gap? Note added to provide details regarding the glands. Airpack will provide glands as per the purchase order.
9 |  | 02 | 4 | Should be revised. position off should be removed according comments of wiring diagram document. | Updated.
10 |  | 02 | 4 | - Panel thickness shall be 2 mm. - Cable gland and Gap is scope of vendor should be mentioned. add to table - Material should be SS316 as per spec of project - - Earth stud should be considered. | 2mm is not a standard panel thickness. 1.5mm Junction boxes will be supplied as per the purchase order. Please provide more details on where this is specified in your specifications. According to Airpack, 2mm thick panels are only required for Unit Control Panels located indoors (N278-000-CI-JSS-1520-001-02 Supply specification for Cabinets and Panels, point 5.1. Point 16 for Termination Panels will be followed.) Changing this will incur additional costs and project delays. Please see point 8 regarding the cable glands and Gap. Junction boxes to be sheet steel as per purchase order. Changing this will incur additional costs and project delays. Earth stud added to drawing.
11 |  | 02 | 4 | All Emergency PBs & Switches in LCP or UCP shall have a protective cover to avoid inadvertent shutdown. | This is standard Airpack practice, note added.
12 |  | 02 | 4 | As per TCL, lamp test Push button should be added | Updated as per the latest P&ID.
13 |  | 02 | 5 | cable gland and Gap should be added to the list | Comment unclear, what is meant by Gap? Note added to provide details regarding the glands. Airpack will provide glands as per the purchase order.
14 |  | 02 | 6 | - Panel thickness shall be 2 mm. - Cable gland and Gap is scope of vendor should be mentioned. add to table - Material should be SS316 as per spec of project - Earth stud should be considered. | 2mm is not a standard panel thickness. 1.5mm Junction boxes will be supplied as per the purchase order. Please provide more details on where this is specified in your specifications. According to Airpack, 2mm thick panels are only required for Unit Control Panels located indoors (N278-000-CI-JSS-1520-001-02 Supply specification for Cabinets and Panels, point 5.1. Point 16 for Termination Panels will be followed.) Changing this will incur additional costs and project delays. Please see point 8 regarding the cable glands and Gap. Junction boxes to be sheet steel as per purchase order. Changing this will incur additional costs and project delays. Earth stud added to drawing.
15
16
17
18
19
20
21
22
23