## Resolution Sheet
|  |  |  | PROJECT: | Integrated Methanol and Ammonia Plant
COMMENT RESOLUTION SHEET FOR: |  |  |  |  | DOC TITLE: | DOC No:
[5 empty] | Instrument Cable Schedule | N-278-VD-6019-IN-SCH-0044-01 (17735-52)
Item no. | Reference | Revision | Status | Client Comments | AirPack's Reply #1 | Client Reply #1 | AirPack's Reply #2 | Client Reply #2
1 | 3 | 01 |  | This document should be revised based on latest comments of relevant Documents (Wiring Diagram (including Terminal Diagram) for LCP Panel and Junction Box). | Noted. This document is updated according to per latest wiring diagram. | noted. Refer to comments on The latest revision of the document
2 | 3 | 01 |  | Plz Next revision of instrument data sheet shall be submitted after Wiring Diagram document finalization. | Please put the comment in the correct document. This cable schedule is updated according to per latest wiring diagram. | Noted.
3 | 3 | 01 |  | Compatibility with other vendor documents including PID and Wiring diagram is vendor responsibility and scope. | Noted. | Noted.
4 | 3 | 01 |  | Cable code identification should be mentioned as per spec of project.(Attachment#1) | Noted. Cable code will be added. | Noted.
5
6
7 | [8 empty] | Open
8 | [8 empty] | Closed
9
10
11
12
13
14
15
16
17
18
19
20