## Resolution Sheet
|  |  |  | PROJECT: | Integrated Methanol and Ammonia Plant
COMMENT RESOLUTION SHEET FOR: |  |  |  |  | DOC TITLE: | DOC No:
[5 empty] | Instrument Cable Schedule | N-278-VD-6019-IN-SCH-0044-01 (17735-52)
Item no. | Reference | Revision | Status | Client Comments | AirPack's Reply #1 | Client Reply #1 | AirPack's Reply #2 | Client Reply #2
1 | 3 | 01 |  | This document should be revised based on latest comments of relevant Documents (Wiring Diagram (including Terminal Diagram) for LCP Panel and Junction Box). | Noted. This document is updated according to per latest wiring diagram. | noted. Refer to comments on The latest revision of the document
2 | 3 | 01 |  | Plz Next revision of instrument data sheet shall be submitted after Wiring Diagram document finalization. | Please put the comment in the correct document. This cable schedule is updated according to per latest wiring diagram. | Noted.
3 | 3 | 01 |  | Compatibility with other vendor documents including PID and Wiring diagram is vendor responsibility and scope. | Noted. | Noted.
4 | 3 | 01 |  | Cable code identification should be mentioned as per spec of project.(Attachment#1) | Noted. Cable code will be added. | Noted.
5 | 3 | 02 |  | cable type to be 20C1.501ARGYN | Updated to 14C1.501ARGYN based on comments provided on the wiring diagram.
6 | 3 | 02 |  | cable type to be 4C1.501ASRDN | Updated.
7 | 3 | 02 |  | cable type to be 19P0.7511ARGYN | Updated. |  |  |  | Open
8 | 3 | 02 |  | cable type to be 1P1.501ARGYN | Updated. |  |  |  | Closed
9 | 3 | 02 |  | these glands on JB or local panel so are in vendor scope of work. Please specift gnald size. | This is not correct, the document states that these glands are on the customer's side and therefor not in Airpack's scope. This information should be provided by the contractor. Changed to TBA (To Be Advised).
10 | 3 | 02 |  | cable length to be added in table | Updated.
11 | 3 | 02 |  | This document should be updated as per latest comment on wiring diagram LCP and JB document. | Updated.
12
13
14
15
16
17
18
19
20