## Resolution Sheet
|  |  |  | PROJECT: | 17811
COMMENT RESOLUTION SHEET FOR: |  |  |  |  | DOC TITLE: | DOC No:
[5 empty] | P&ID | 17811-03
Item no. | Reference | Revision | Status | Client Comments | AirPack's Reply #1 | Client Reply #1 | AirPack's Reply #2 | Client Reply #2
General |  | 0 | Closed | Please provide all tagnumbers according to client numbering procedure, this procedure is not available |  | Project numbering procedure is attached. | noted
1 | page 1 | 0 | Closed | Please specify | discharge temperature is 190°C, this will be added in next revision | Purchaser believes that the reported temperature is based on the outlet pressures beyond the operting condition. As a result purchaser can only emphesize on after cooler temperature guarantee, and vendor shall under take the responsibility of outlet temperature and its impediments to compressor performance. | temperatures are based on PSV set-point, which is the required design condition for the compressor. As it would be technacilly possible that this is reached in case of failure of any items. This is also where the compressor design temperature and pressure come from. we will specifiy the actual operating temperature in the compressor data sheet as discussed during the meeting
2 | page 1 | 0 | Closed | Discrepancy between flow rate? | there is no discrepancy between the flow rates, compressor flowrate is more than the required flow, this is the smalles watercooled compressor in our scope. | Recycling line is the waste of energy that vendor imposed on these compressor packages. However, it is incombent upon vendor to under take the pertinent consequences. | you are correct, however since client wants a water cooled machine this is the smalles compressor available with water cooling. We can change back to air cooled, then the power consumption will be lower or keep this and take the addition consumption.
3 | Page 1 | 0 | Closed | Please report the compressor capacity 114 Kg/h according to DSH of the project as well. | Noted will be added in next revision | Closed. | closed
4 | page 1 | 0 | Closed | PG is required | Pg is not required, there is alreade PG on the main line. | Vendor declares that PG has already been installed on the main line. However due to wide range of unloader valves pressure range toleration (4 to10 bara) vendor states that regulating valve is not needed. | This will be confirmed, we are checking the operating range of the valve to be sure. In case it is require we will add in in the next revision.
5 | page 1 | 0 | Closed | Please specify, is it pressure regulating valve? | this is filter | Closed. | closed
6 | page 1 | 0 | Closed | Please specify | Will be specified as soon as all information is available | Closed. | closed
7 | page 1 | 0 | Closed | If actuator of control valve is pneumatic type, instrument air line shall be shown | Noted instrument air line will be shown | Closed. | closed |  | Open
8 | page 1 | 0 | Closed | -Please add line number as per project requirement. - Please specify battery limit. - Please clarify separate instrument air for utility connection is required or not. | - Noted line numbers will be added - Noted battery limit will be added - can be done internal with nitroge, however is you prefer IA, then we can add it. | -Closed. -Closed. -Closed. AIRPACK can use his own source of utility instead of instrument air. | all closed |  | Closed
9 | page 1 | 0 | Closed | The max return pressure can be 3.5 bara (2.5 barg) The max return temperature can be 45°C | Noted this will be updated | Closed. | closed
10 | page 1 | 0 | Closed | Please add FT | Why FT for cooling water is required? | Referring to clause M7 of TCL AIRPACK agrees that they will supply and installed FT at cooling water outlet line. | FT added in next revision
11 | page 1 | 0 | Closed | Please check the pipe size in order to avoid contact of TW with pipe. | Design will be checkec by our engineering department. | Closed. | closed
12 | page 1 | 0 | Closed | FO/FC must be shown | Noted will be added in next revision | Closed. | closed
13 | page 1 | 0 | Closed | Please add check valve. | check valve is not required,, PCV is FC | Purchaser believes that failed open (FO) PCV with check valve are required, and vendor is opposed to this idea. Therefore, this issue and the decision to be made is postponed to HAZOP meeting.AIRPACK will follow HAZOP results for that matter. | after discussiong with my managment, it is clear PCV should be FC. In any case it will be discussed during HAZOP.
14 | page 1 | 0 | Closed | Please add VT | Vibration monitoring is not included. As per TQ | Referring to clause M30.1 of TCL AIRPACK will supply and provide vibration transmitter(VT) and the signals shall be sent to UCP. | VT will be added in next revision
15 | page 1 | 0 | Closed | inlet and discharge size of all PSV shall be specified. | Noted will be added as design of check valve is confirmed | Closed. | closed
16 | page 1 | 0 | Closed | Specify the location of discharging | will be specified as safe location | Closed. | closed
17 | page 1 | 0 | Closed | Please show the motor signal such as running, fault and etc. | They are available on the second page | Closed. | closed
18 | page 1 | 0 | Closed | Please show electrical heater with required power | Noted will be added in next revision | Closed. | closed
19 | page 1 | 0 | Closed | Please specify drain size. | Noted will be added in next revision | Closed. | closed
20 | page 1 | 0 | Closed | level transmitter shall be added | We have to confirm whether this is possible at all, because of the limited ammount of connection o this oil sump. Also since this an oil free compressor there is no oil consumption, so it shoulc not be really required. | With reference to clause M30 of TCL LT is required. AIRPACK claimes that LT may not be installed due to small size of oil sump and they will revert to purchaser in next revised P&ID. | Please find the picture of the oil sump as you can see it is very clear there is no way to connect a level transmitter anywhere. The oil sum only contain a level of 20 cm which is not realy measurable as well.
21 | page 1 | 0 | Closed | Before all PSV isolating valve (LO) shall be used. | as per TQ this is deviated | Purchaser believes that block and blow off valve is necesary for the safety of operator and maintenance people , and vendor is opposed to this idea. Therefore, this issue and the decision to be made is postponed to HAZOP meeting.AIRPACK will follow HAZOP results for that matter. | we will follow the outcome of the HAZOP. However since we have taken a devation on this, if the outcome is that the valve needs to be added the cost will be for client
22 | page 1 | 0 | Closed | Please show the connection for all instruments | Noted will be added in next revision | Closed. | closed
23 | page 1 | 0 | Closed | Please add check valve at cooling water inlet | this is not required | Referring to TCL (clause M7) check valve is required. AIRPACK confirmes that they will provide and supply accordingly. | CV will be added in next revision
24 | page 1 | 0 | Closed | Supply pressure: 4.5 bara Temperature: 35°C | Noted will be changed and updated | Closed. | closed
25 | page 1 | 0 | Closed | Provide symbol and legend sheet. | Not required as it is as per your legend | Confirmed and closed. | closed
26 | page 1 | 0 | Closed | Specify vendor scope of supply. | as per P&ID | AIRPACK states that whatever indicated on P&ID is on their scope of work and supply. | closed
1 | page 1 | 0 | Closed | Duplicate tag no. | Noted, will be updated | Closed. | closed
2 | page 1 | 0 | Closed | Level gauge connection shall be modified and isolation valves shall be specified | Not possible this is intigrated level on the compressor oil sump | Noted. | as is visible on the picture of the compressor above, you van se the level gauge.
3 | page 1 | 0 | Closed | - Junction boxes, LCP, UCP tag no shall be specified. - Package's cable scope of supply shall be specified with limit of supply sign | -Noted will be specified - all cable inside the package are in Airpack scope external connection in client scoper | Closed. | closed
4 | page 1 | 0 | Closed | Please check Fault alarm requirement | We have alarm and trip, no fault alarm required | Noted. AIRPACK will send revised P&ID. | Fault alarm not required, only alarm and trip have been included.
5 | page 1 | 0 | Closed | Please clarify about compressor operational and compressor running signals | This will be clarified in control philosophy | Noted. | closed
6 | page 1 | 0 | Closed | - Size and rating for all valve and PSV shall be shown in PID. - Thermowell's flange shall be shown in PID. - Thermowell tag no. are duplicated. | - noted will be added - noted will be shown - noted will be updated | Closed. | noted will be added when information is available.
1 | Page 3 | 1 |  | Please calculate discharge temperature again. With reference to Thermodynamic formula (T2/T1= P2/P1 K-1/K discharge temperature is much less than 190 C. Please recalculate again with using discharge pressure not design pressure. | Adiabatic is not always completely accurate, we do calculation with a dedicated program for our compressor which takes into account the actual conditions, like humidity which are not taken into account in your standard formula, after final calculation discharche temperature is 180°C at 21 bara | Please calculate discharge temperature again. With reference to Thermodynamic formula (T2/T1= P2/P1 K-1/K discharge temperature is much less than 180 C. Using mentioned formula, adiabatic temperature is 148 C.
2 | Page 3 | 1 |  | All signals that display in your UCP share screen shall be indicate same bellow schematic.(for symbol and legend please refer to attached file) | Noted will be updated | Closed.
3 | Page 3 | 1 |  | Considering the fact that 1 1/2" is met the criteria. Please check if 1 1/2" can be used. | as per original it was 2", also the outlet is 2", either we update both or we keep both at 2" | Closed.
4 | Page 3 | 1 |  | Considering the fact that the "20-C-7080" is supposed to compress "Instrument Air", NL is meaning less and all line numbers must be revised. | Noted will be updated | Closed.
5 | Page 3 | 1 |  | Tag to be modify | Noted will be updated | Closed.
6 | Page 3 | 1 |  | It seems that discharge PT shall send signal to solenoid valve. Please show signal which open and close the solenoid valve. | Noted will be updated | Closed.
7 | Page 3 | 1 |  | Solenoid valve input signal shall be shown. | Noted will be updated | Closed.
8 | Page 3 | 1 |  | On/Off valve tag no. shall be specified | Noted will be updated | Closed.
9 | Page 3 | 1 |  | PID No.: BU-20-D-700-PR-PID-711 Line No.: 1 1/2"-CWS-7001-500C(N) | Noted will be updated | Closed.
10 | Page 3 | 1 |  | According to S&A list HH Alarm is reported 21 .No inconsistency must be seen between documents. | Alarm and trip list will be updated according to this latest P&ID | Closed
11 | Page 3 | 1 |  | According to pulsation damper data sheet OT/DT are reported 5-55 oC /80 oC .No inconsistency must be seen between documents. | Datasheet will be updated where required | Closed
12 | Page 3 | 1 |  | According to pulsation damper data sheet OP/DP are reported 21.5 bara/26 bara .No inconsistency must be seen between documents. | Datasheet will be updated where required | Closed
13 | Page 3 | 1 |  | According to After Cooler data sheet DP is reported 25 barg. No inconsistency must be seen between documents. | Noted P&ID is updated | Closed
14 | Page 3 | 1 |  | Temperature shall be recalculated again. | Adiabatic is not always completely accurate, we do calculation with a dedicated program for our compressor which takes into account the actual conditions, like humidity which are not taken into account in your standard formula, after final calculation discharche temperature is 180°C at 21 bara | Temperature before cooling to be less than 150 deg C . AIRPACK shall provide aftercooler(Water cooled) .Aftercoo ler outlet gas temperature to be 40 deg C. Therefor compressor dishcharge temperature shall be less than 150 °C. Please refer to clause M29 of TCL.
15 | Page 3 | 1 |  | The Compressor is supposed to start by means of a low-pressure switch on delivery pipe and to stop when high pressure is reached. The required low/high pressure switches to maintain the required delivery pressure shall be considered. The highlighted control loop does not meet the requirement and must be modified. | Noted, after final confirmation we have removed the recycle line in favour of loading / unloading of the compressor through the compressor valves. | Closed
16 | Page 3 | 1 |  | Symbol, Legend and abbreviation same as attached file shall be submitted by vendor. | Legend as per format of client, no need to at separate legend | Noted, client symbol and legend is general for whole of project but you must prepare legend in your scope of work based on format of client.
17 | Page 3 | 1 |  | Please add in general note: All signals mentioned in P&ID will be transferred to FCS via Modbus TCP/IP communication link. | Noted will be updated | Closed.
18 | Page 4 | 1 |  | Solenoid valves shall be I.S. with 24 VDC voltage rating. | solenoid are Exd not Exi | As per MRQ clause 3.17.28 and ESS for package "Solenoid valves shall be I.S. with 24 VDC voltage rating."
19 | Page 4 | 1 |  | JIDX-C7080-xx xx=your sequence | Noted will be updated | Closed.
20 | Page 4 | 1 |  | Please specify cable size and type as per attached files. | No file receive, in any case it is not required to be shown on this drawing | Noted, it should be indicate in related documents.
21 | Page 4 | 1 |  | JIAX-C7080-xx xx=your sequence | Noted will be updated | Closed.
22 | Page 4 | 1 |  | LP-C7080-01 | Noted will be updated | Closed.
23 | Page 4 | 1 |  | UCP-C7080-01 | Noted will be updated | Closed.
24 | Page 4 | 1 |  | Redundant Ethernet Modbus TCP/IP to FCS | Noted will be updated | Closed.
25 | Page 4 | 1 |  | Following signals shall be considered from UCP from/to ESD(HWC) via hardware connection : • HS-715-1R-1(Reset) • HS-715-SD-1(Emergency Shutdown Command) • I-715-MOS-1(Maintenance Override Switch) • XAL-715-2(Common Alarm) | Reset and MOS switch are not used by use and not required. Other signals are incorperated | Regarding to ESD command to the compressor so reset command (HS-715-1R-1) is required to consider, and in order to override compressor from ESD system MOS switch (I-715-MOS-1) is required. As per project C&E and PID mentioned signals are required vendor must consider that signals or propose a reply.
26 | Page 4 | 1 |  | Following signal shall be considered from FCS to UCP via hardware connection : • XS-715(Interlock Switch Stop Compressor) • XCS-715(Time Synchronisation) | Signals are incorperated | Closed.