## Resolution Sheet
|  |  |  | PROJECT: | 17811
COMMENT RESOLUTION SHEET FOR: |  |  |  |  | DOC TITLE: | DOC No:
[5 empty] | Instrument datasheets | 17811-12
Item no. | Reference | Revision | Status | Client Comments | AirPack's Reply #1 | Client Reply #1 | AirPack's Reply #2 | Client Reply #2
General | page 1 | 0 | Open | 1. Compressor tag number must be added | Will be incorporated in the next submission. | Noted.
1 | page 1 | 0 | Open | 2. Maximum ambient temperature must be considered 52°C | Will be incorporated in the next submission. | Noted.
2 | page 1 | 0 | Open | All instrument tag no shall be revised base on comment on PID | Will be incorporated in the next submission. | Noted for nitrogen comp. but for air comp. to be modified.
3 | page 1 | 0 | Closed | Manufacturer and model no. for all devices shall be specified | Will be submitted after purchase. | Noted.
4 | page 1 | 0 | Closed | This document is checked only for compressor 7080. New document should be generated for compressor 1002. | Will be incorporated in the next submission. | Noted.
5 | page 1 | 0 | Open | Drawing shall be match the title of the project title block | There are no drawings in this document. | All page of data sheet to be in project title block.
6 | page 2 | 0 | Closed | These are not instrument valve so te be deleted from this doc. | Will be incorporated in the next submission. | Noted.
7 | page 3 | 0 | Closed | As per project spec. Diaphragm element pressure gauge shall be specified for meausuring pressures belllow 1 bar | Will be incorporated in the next submission. | Noted. |  |  | Open
8 | page 3 | 0 | Open | As per project spec. to be 1/2" | For PDG 1/4" is standard connection, 1/2" not available. Airpack will supply 1/4"/ 1/2" connectors. | As per project specification PDG connection shall be 1/2" NPT. Please review other vendors data sheet. |  |  | Closed
9 | page 4 | 0 | Closed | All comments on instruments od 20-C-1002 applicable for instrument on 20-C-7080 too | Will be incorporated in the next submission. | Noted.
10 | page 5 | 0 | Closed | Please be noted that process connection size of manifold to be 1/2" NPTF | Will be incorporated in the next submission. | Noted.
11 | page 7 | 0 | Closed | To be completed as per instrument index | Will be incorporated in the next submission. | Noted.
12 | page 7 | 0 | Closed | Line or equipment number to be specified for all instrument | Will be incorporated in the next submission. | Noted.
13 | page 7 | 0 | Open | Gauges with max. scale value of 25 bar(g) and more shall be solid front. | Will be incorporated in the next submission. | This comment was not impleamented, please refer to comment on document.
14 | page 7 | 0 | Closed | Oil filled case shall be considered for vibration proof where pulsaion and are expected. | Will be incorporated in the next submission. | Noted.
15 | page 9 | 0 | Closed | Pulsation dampers shall be furnished for all gauges on the discharge side. | Will be incorporated in the next submission. | Noted.
16 | page 10 | 0 | Closed | Hermetically sealed case is required for all TE. | Will be incorporated in the next submission. | Noted.
17 | page 10 | 0 | Open | The dial shall be every angle type | This is for local assembly, not for panel mounted assembly | Local assembly temperature gauge must be every angle type, as per project spec.
18 | page 10 | 0 | Closed | Over range protection shall be higher than or equal to 130% of the maxi. Scale value. | Overrange protection is not available for temperature gauges. | Noted.
19 | page 11 & 21 | 0 | Closed | rating will be checked after receiving data for pipeclass. | Rating is as mentioned in the P&ID | Noted.
20 | page 11 & 21 | 0 | Closed | Roughness (125-250AARH) to be mentioned | Will be incorporated in the next submission. | Noted.
21 | page 11 & 21 | 0 | Open | Length to be mentioned as per table. | Thermowell length will be determined, pending on the branch length en thermowell tip on middle 2/3 part of pipesize. This is commom engineering practise. | Airpack must specify thermowell length so that with considering TW nozzle projection, thermowell tip stay on middle third of pipe, so you must specify U length in this stage in the data sheet.
22 | page 11 | 0 | Closed | Chain and plug shall be considered for all tW. | This is not specified and not part of our supply. | Noted.
23 | page 11 | 0 | Open | Vendor to provide wake frequency calculation to asme PTC 19.3 | This calculation is not part of our agreed supply. | As per project specification 1216-DE-00-IN-ESS-603 page 48 section F : The design of the thermowells shall be verified for all items by vendor by means of stress analysis, resulting from stream velocity condition. Frequency limitation shall meet ASME PTC 19.3 TW-2010. Vendor shall submit the calculation sheets to purchaser for approval.
24 | page 14 & 21 | 0 | Closed | VTA to be specified | Will be submitted after purchase. | Noted.
25 | page 14 | 0 | Closed | for LG -vent drain connection size / vessel rating 1", 300# RF) | The LG is not for a vessel but a small Oil reservoir, connection 1/2" NPT-F are suffiecient for available space. | Noted.
26 | page 15 & 20 | 0 | Closed | 2 Input for elec. Connection shall be considered | This is not specified and 1x enty is part of our supply. | Noted.
26 | page 15 | 0 | Closed | Normal connections for pressure transmitter will be NPT 1/2" F unless flange connections are required. | For pressure transmitters standard connections are 1/2" NPT-M | Noted.
26 | page 15 | 0 | Closed | sensor fill fluid to be clarified | Standard pressure transmitters have sensor fill fluid, the type is depending on the manufacturer. | It should be specified after your sub-vendors are specified.
26 | page 28 | 0 | Closed | solenoid seal to be specified as per piping class | Valves are in tubing no piping class applicable, material will be suitable for the conditions mentioned. | Noted.
26 | page 28 | 0 | Closed | Solenoid valve signals shall be Ex IA | as per TCL M33 not required, it will be Exd | Noted.
26 | page 28 | 0 | Closed | Atex certificate required. | Will be incorporated in the next submission. | Noted.
26 | page 29 | 0 | Open | Solenoid valve to be installed on shut down valve, please add required data. | Solenoid valve will be assembled seperately not on the valve/Actuator. For better maintenance en reachabiity in the skid. | vendor reply is not accepted, solenoid is one of the on-off valve accessories it shall be removed from this data sheet and mentioned in on-off valve data sheet as an accessories.