## Resolution Sheet
PROJECT:
COMMENT RESOLUTION SHEET FOR: |  |  |  |  | DOC TITLE: | DOC No:
[5 empty] | Instrument Index | 17811-72
Item no. | Reference | Revision | Status | Client Comments | AirPack's Reply #1 | Client Reply #1 | AirPack's Reply #2 | Client Reply #2
1 | 1 | 00 | Closed | As I/O list did not supplied by vendor so all required items in I/o list to be added to index. -Signal Type (4-20mAmp, 24vdc , ...) -From/ To And also all signals to be indicated in this doc (limit switch of valves , remote start stop command (refer to page 4&6 OF pid) | Noted. Additional I/O information will be added to the existing instruments, and signals to/from ESD/FCS/DB will be added as per P&ID. | Noted.
2 | 1 | 00 | Closed | This document is checked only for compressor 7080. New document should be generated for compressor 1002. | New documents will be one instrument index for compressor 1002, and one for compressor 7080. | Noted.
3 | 3 | 00 | Open | As per project spec redundancy to be considered where required (for example closed loops) | Noted. Redundant I/O will be indicated. | Redundancy is not specified, please modify.
4 | 3 | 00 | Open | To be corrected. | Noted. It will be updated. | PID, Data sheet, wiring and Hook-up document number shall be modified as per VPIS.
5 | 3 | 00 | Open | There is deviation between this doc and PID in sequence of tag numbers , please clarify? | The tag numbers will be updated according to per P&ID. | Please refer to comment on nitrogen PID for instrument numbering procedure.
6 | 3 | 00 | Closed | To be filled carefully,there is not any signal for local gauges. | Noted. The signals for local gauges will be removed. | Noted.
7 | 3 | 00 | Closed | Refer to comments on data sheet. | Noted. It will be udpated according to per data sheet. | Noted. |  |  | Open
8 | 3 | 00 | Closed | isolation valve for LG to be considered. | As per P&ID, there's no isolation valve for LG. | Noted. |  |  | Closed
9 | 3 | 00 | Closed | For on/off valve DO signals will be considered for solenoid valve not ball valves. | Noted. It will be updated. | Noted.
10 | 3 | 00 | Closed | following items to be added to index: VT FT | Noted. It will be incorporated. | Noted.
11 | 3 | 00 | Closed | Same ascomment on C-1002 | Noted. | Noted.