## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 21/Aug/2020 | Rev.:
|  | Comment Sheet Ref.No.: | Doc Description:
|  | Transmittal No.: | Doc. No.:
|  | Transmittal Date: | Doc Rev.:
Item | CHCE Comment |  |  | Vendor Clarification |  |  | CHCE Comment
1 | Acc. to TCL, It shall be 55KW. |  |  | The absorbed power of the compressor is only 37 kW and therefore 45 kW is correct, this was a mistake in the offer. It does not have any impact on the design |  |  | closed
2 | Specify Synchronous speed of the motor. |  |  | Noted and updated |  |  | closed
3 | Please specify exact value. |  |  | Noted and updated |  |  | this item shall be specify from vendor mechanical data sheet .
4 | Put it in project's cover sheet. |  |  | Noted and updated |  |  | closed
5 | Change to ferromagnetic material. |  |  | Noted and updated |  |  | this item has not been correct . Please revised it.
6 | Change to 5010. |  |  | Noted and updated |  |  | this item has not been correct . Please revised it.
7 | IP65 |  |  | additional cost for this was not accepted, will stay IP56 unless offer is officially accepted, however the motor order is on hold because of this point, which will now immediatelly impact the deilvery time. |  |  | closed.
8 | Please be noted that we consider C-1002 as a feeder type, not a motor. Cable size & cable entry for feeder type is: Cable: (3C+N)-150mm2 Gland: EX-IP65(E/M63) Cable from panel to motor is in vendor's scope of work. |  |  | Noted we will add our cable information |  |  | closed.
9
10
11
12
13
14
15
16
17