## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 16/Nov/2021 | Rev.:01
|  | Comment Sheet Ref.No.: | Doc Description: INSTRUMENT INDEX FOR EMERGENCY INSTRUMENT AIR COMPRESSOR
|  | Transmittal No.: APCES-V-00051 | Doc. No.: BU-20-VD-303-IN-INX-0083
|  | Transmittal Date: 16/Nov/2021 | Doc Rev.: 01
Item | CHCE Comment |  |  | Vendor Clarification |  |  | CHCE Reply
1 | As I/O list did not supplied by vendor so all required items in I/o list to be added to index. -Signal Type (4-20mAmp, 24vdc , ...) -From/ To And also all signals to be indicated in this doc (limit switch of valves , remote start stop command (refer to page 4&6 OF pid) |  |  | Noted. Additional I/O information will be added to the existing instruments, and signals to/from ESD/FCS/DB will be added as per P&ID. |  |  | Noted
2 | This document is checked only for compressor 7080. New document should be generated for compressor 1002. |  |  | New documents will be one instrument index for compressor 1002, and one for compressor 7080. |  |  | Noted
3 | As per project spec redundancy to be considered where required (for example closed loops) |  |  | Noted. Redundant I/O will be indicated. |  |  | Redundancy is not specified, please modify.
4 | To be corrected |  |  | Noted, it will be updated |  |  | PID, Data sheet, wiring and Hook-up document number shall be modified as per VPIS.
5 | There is a deviation between this doc and PID in sequence of tag numbers, please clarify? |  |  | The tag numbers will be updated according to per P&ID. |  |  | Please refer to comment on nitrogen PID for instrument numbering procedure.
6 | To be filled carefully,there is not any signal for local gauges. |  |  | Noted. The signals for local gauges will be removed. |  |  | Noted
7 | Refer to comments on data sheet |  |  | Noted. It will be udpated according to per data sheet. |  |  | Noted
8 | isolation valve for LG to be considered |  |  | As per P&ID, there's no isolation valve for LG. |  |  | Noted
9 | For on/off valve DO signals will be considered for solenoid valve not ball valves |  |  | Noted, it will be updated |  |  | Noted
10 | following items to be added to index: VT FT |  |  | Noted, it will be incorporated |  |  | Noted
11 | Same as comment on C-1002 |  |  | Noted |  |  | Noted
Rev.01
12 | *Reply sheet shall be submitted by vendor *Please refer to comment in PID for instrument numbering procedure *PID, data sheet, wiring and hook-up document number shall be modified as per VPIS *This document will be finalized after PID and data sheet approval and considered all comments *PSV-1001 shall be added to teh instrument list *Manufacturer adn model no. to be specified in this document |  |  | Noted |  |  | These comments are related to the nitrogen compressor,
13 | Abbreviation to be specified. Please clarify about "DB" |  |  | Distribution board |  |  | Noted.
14 | Tag number to be specified |  |  | Please advise |  |  | Please refer to numbering procedure and PID legend.
15 | Please select as per standard range |  |  | It's according to instrument data sheet |  |  | Range 0~35 shall be modified as per standard range of pressure gauge in this document and data sheet too.
16 | Process connection 1/2" NPT-F |  |  | It's according to instrument data sheet |  |  | Noted.