## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 10/Dec/2021 | Rev.:01
|  | Comment Sheet Ref.No.: | Doc Description: COMPRESSOR MOTOR OUTLINE DRAWING & TERMINAL BOX WIRING DIAGRAM FOR NITROGEN GAS BOOSTER
|  | Transmittal No.: APCES-V-00066 | Doc. No.: BU-20-VD-303-EL-DWG-0053
|  | Transmittal Date: 10/Dec/2021 | Doc Rev.: 01
Item | CHCE Comment |  |  | Vendor Clarification |  |  | CES Reply
1 | Compressor tag number must be added. |  |  | Noted |  |  | Refer to document
2 | This document is checked only for compressor 7080. New document should be generated for compressor 1002. |  |  | Noted
3 | EL.06: Cable ad Gland size is attached. |  |  | Noted |  |  | Refer to document
4 | EL04: Terminal box inside arrangement drawing shall be submitted. |  |  | Noted |  |  | Noted
5 | EL01: Motor finish color shall be submitted. |  |  | Is specified in the datasheet and painting specificaiton |  |  | Noted
6 | EL02: Hole and cable gland size shall be submitted. |  |  | noted |  |  | Noted
7 | EL03: Earth stud details shall be matched with attached DETAIL"A". |  |  | Not possible on a motor, earth connections have been speciied in new drawing |  |  | Vendor shall confirm that: Earth stud details shall be matched with attached DETAIL"A".
8 | El.07: The unit of dimension of each part shall be mentioned as a note. |  |  | Noted |  |  | Noted
9 | EL05: Exd |  |  | This is old format form ATEX notification. |  |  | Refer to document