## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 10/Jan/2022 | Rev.:02
|  | Comment Sheet Ref.No.: | Doc Description: SINGLE LINE DIAGRAM FOR POWER DISTRIBUTION PANEL FOR EMERGENCY INSTRUMENT AIR COMPRESSOR
|  | Transmittal No.: APCES-V-00081 | Doc. No.: BU-20-VD-303-EL-DIG-0097
|  | Transmittal Date: 10/Jan/2022 | Doc Rev.: 02
Item | CHCE Comment |  |  | Vendor Clarification |  |  | CES Reply
1 | EL.02: Required circuit breakers shall be considered and shown it in POWER DISTRIBUTION PANEL. (for Incoming and Outgoings ) |  |  | Updated in next revision CES REPLY: Please see comment inside document |  |  | It has not been added in the document yet.
2 | EL.01: Add following data in the box. From: SWB3A-03(0.4KV) Cable no: EBP-20-C-7080-M Cable Type and Size: CU/XLPE/AWA/PVC3.5*50mm2 Gland: EX-IP66, C2/M40 |  |  | Updated in next revision CES REPLY: Please see comment inside document |  |  | Noted
3 | Comments Rev.01 below
4 | EL.01: Add following data in the box. From: SWB3A-03(0.4KV) |  |  | Updated in next revision |  |  | Noted
5 | EL.02: Required circuit breakers shall be considered and shown it in POWER DISTRIBUTION PANEL. (for Incoming and Outgoings ) |  |  | Mcb's are used for incoming power as project specification |  |  | It seems that using MCB for incoming is not suitable. Additional information (sizing) shall be announced.
6 | Please clarify about connection between UCP and PDP with 20x1 mm2 cable. |  |  | This is the multicore cable for all the signals between the UCP and PDP check wiring diagram |  |  | According to cable schedule 10Px0.75mm2 has been considered
7 | EL03:this document should have SLD structure, but it is similar to a block diagram, not a single line diagram |  |  | This is the Airpack single line diagram as per project specification |  |  | Attached sample SLD shall be taken into consideration by airpack
8 | Redundant UPS power supply to UCP to be specified. |  |  | Redundant power supply in used for the UCP |  |  | Noted, but it must be specified in the document.