## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 10/Feb/2022 | Rev.:03
|  | Comment Sheet Ref.No.: | Doc Description: I/O LIST FOR EMERGENCY INSTRUMENT AIR COMPRESSOR
|  | Transmittal No.: APCES-V-00094 | Doc. No.: BU-20-VD-303-IN-LST-0084
|  | Transmittal Date: 10/Feb/2022 | Doc Rev.: 03
Item | CHCE Comment |  |  | Vendor Clarification |  |  | CES Reply
1 | PB-71103 on local panel, for compressor ESD PB is missed in I/O list. Please clarify about HM-71101 signal, why are you considering a light for hourmeter? what does this light do? |  |  | ESD button on LP will be added. HM is hourmeter, without light. The instrument type will be adjusted. |  |  | Noted.
2 | P&ID number to be modified as per related P&ID document number. |  |  | Noted. It will be incorporated. |  |  | Noted.
3 | Nitrogen" to be modified to "Air" Please modify other description if required |  |  | Noted. It will be incorporated. |  |  | Noted.
4 | (Unload/Stop) |  |  | Noted. It will be incorporated. |  |  | Noted.
5 | To be specified |  |  | Noted. It will be incorporated. |  |  | Noted.
6 | Please modify to "-" |  |  | Noted. It will be incorporated. |  |  | Noted.
7 | State 0 must be Off/Local |  |  | Noted. It will be incorporated. |  |  | Noted.
8 | State 1 must be Remote only |  |  | Noted. It will be incorporated. |  |  | Noted.
9 | Tag no. shall be specified |  |  | Please advise the tag numbers. |  |  | Noted.
10 | FCS |  |  | Noted. It will be incorporated. |  |  | Noted.
11 | - Signal for PY-71101 is missed - Please add I/O summary table for each I/O type. |  |  | Noted. It will be incorporated. |  |  | Noted.
12 | Please fill xx as your sequence HS-711xx-R HS-711xx-SD XS-711xx-ST/SP XS-711xx-ST/SP XL-711xx YAL-711xx XL-711xx YAL-711xx |  |  | Noted. It will be incorporated. |  |  | Noted.
| .- AO signal type shall be added. - I/O redundancy shall be mentioned |  |  | AO signals is through PID controller I/O reduncacy is mentioned already |  |  | - AO card for control valve must be considered, PID controller is not accepted. - Closed.
| 18/16 |  |  | Noted. It will be incorporated. |  |  | Closed.