## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 07/Feb/2022 | Rev.:03
|  | Comment Sheet Ref.No.: | Doc Description: Calculation & Datasheet of Control valves / On-off valves for Emergency instrument air compressor
|  | Transmittal No.: APCES-V-00093 | Doc. No.: BU-20-VD-303-IN-DSH-0091
|  | Transmittal Date: 07/Feb/2022 | Doc Rev.: 03
Item | CHCE Comment |  |  | Vendor Clarification |  |  | CES Reply | Vendor calarification | CES Reply
1 | All page of datasheet to be in project title block. |  |  | Format can't be changed for this document, however we will add contracter and client logo in each page. |  |  | Closed.
2 | P&ID number to be modified as per related P&ID document number for all instruments. |  |  | Updated in next revision |  |  | Closed.
3 | Line number of each PSV shall be specified. |  |  | Updated in next revision |  |  | Closed.
4 | According to PID, solenoid valve as an accessories shall be considered for On-off valve. |  |  | According P&ID Solenoid valves have a seperate TAG-no. Thus considered as a seperate item with corresponding datasheet. |  |  | Solenoid valve's tag shall be same as its on-off valve's tag sequence. Solenoid valve is an important accessories in on-off valves so one section must be assigned for this issue and specified general data such as tag no., signal type, ex protection, area classification, material and etc. | Solenoid datasheet is part of 17811-12B Instrument datasheets. Cross-reference updated on next revision. | Closed.
5 | Leakage class shall be specified. |  |  | Updated in next revision |  |  | Comment is not implemented in the document. | updated in next revision | Closed.
6 | Trim, seat, ball, stem etc.material shall be specified. |  |  | Updated in next revision |  |  | Project PMS as mentioned in the document shall be followed by vendor. | updated in next revision | Closed.
7 | Please clarify why 2 pneumatic connection is required. |  |  | This is standrad for pneumatic actuator, for single action 1x will be used, for double acting 2x will be used. |  |  | Noted, Closed.
8 | Actuator yoke and housing shall be carbon steel. |  |  | Rack&pinion type actuator do notvhave a yoke and casrbon steel housing is not available. Aluminium epoxy coated is Airpack standard and suitable for this application en evironment. |  |  | Noted, Closed with vendor guarantee for environmental condition. | noted | Closed.
9
9 | PV-71101 datasheet and calculation sheet shall be added. |  |  | Updated in next revision (calculation sheet VTA) |  |  | Closed.
12 | All check valve and hand valve shall be deleted. |  |  | There is no separate document for this they will be kept here and need to be checked. |  |  | There is no need to submit data of manual valve and check valve. There is no need to add any document regarding manual valve and check valve in VPIS. It is in airpack responsibility to purchase all valves as per project requirements.Data of manual valve and check valve shall be removed.
13 | These valves will not be checked… |  |  | See comment 12 |  |  | See item 12
14 | Based on Basis of design of design pressure ….. |  |  | design pressures are as per P&ID. |  |  | PR Reply: Design pressure must be calculated based on Project Criteria.
15 | 500C(N) |  |  | Updated in next revision |  |  | Closed.
21 | Ex'd' certificate for solenoid valve is required |  |  | see comment 4 |  |  | Closed.
22 | Please clarify it is not found in PID |  |  | It is the filter symbol at the Compressor Inlet upstream solenoid XY-71101 |  |  | Tag no shall be specified, also mentioned in P&ID too.
23
23 | Hand valves and check valves will not checked by instrument department and shall be removed from this data sheet. |  |  | It is customer responsibility to check this, if not checked we will assume it is approved. And continue with ordering.
24 | ALL MANUAL VALVE AND CHECK VALVE SHALL BE DELETED. PROJECT SPECIFICATIONS SHALL BE FOLLOWED BY AIRPACK. |  |  | See item 23 |  |  | Closed.
25 | ABM |  |  | Updated in next revision |  |  | Closed.
26 | 8,5 |  |  | Updated in next revision |  |  | Closed.
27 | 52 the comment is valid for all pages |  |  | Updated in next revision |  |  | Closed.
28 | 85 the comment is valid for all "INA" lines |  |  | Updated in next revision |  |  | Closed.
29 | 7 the comment is valid for all "CWS"& "CWR"lines |  |  | Updated in next revision |  |  | Closed.
30 | 100 the comment is valid for all "CWS"& "CWR"lines |  |  | Updated in next revision |  |  | Closed.
31 | 3,5 mr/hr must be double checked |  |  | 1,4 m3/hr as per P&ID will be updated in next revision |  |  | Closed.
32 | Tag no shall be specified, also mentioned in P&ID too. |  |  | No tag nr. mentioned on P&ID |  |  | Airpack prepare documents, conformity of documents is in Airpack responsibility. We cant find this data sheet refer to which item in P&ID, Accordingly tag to be specified, also mentioned in P&ID.
33 | Line no to be specified |  |  | No line no mentioned in P&ID |  |  | Airpack prepare documents, conformity of documents is in Airpack responsibility.
34 | Body material based on ASTM code shall be selected as per line number class from the project PMS. |  |  | Updated in next revision |  |  | Closed.
35 | Following items shall be specified for control valve: CV, travel%, Trim characteristic |  |  | Mentioned in calculation; updated in revision after purchase. |  |  | Noted. Also calculation result shall be mentioned in data sheet
36 | Positioner required data such as follow shall be added to data sheet: Input signal, IP, Pneu.- elec. connection size. |  |  | Mentioned iin line 28, 30, 35 on datasheets IP added in next revision |  |  | Closed.
37 | Positioner shall included with pressure gauge |  |  | Updated in next revision. |  |  | Closed.
38 | Minimum material for wetted part shall be SS316. |  |  | Mentioned in line 21 datasheet. |  |  | Closed.
39 | 85 dBA |  |  | Updated in next revision. |  |  | Closed.
40 | Filter regulator and gauge are required |  |  | Updated in next revision. |  |  | Closed.
41
33