## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 28/Feb/2022 | Rev.: 04
|  | Comment Sheet Ref.No.: | Doc Description: CONTROL PHILOSOPHY FOR NITROGEN GAS BOOSTER INCL. CRS
|  | Transmittal No.: APCES-V-00105 | Doc. No.: BU-20-VD-303-PR-DPH-0046
|  | Transmittal Date: 28/Feb/2022 | Doc Rev.: 04
Item | CHCE Comment |  |  | Vendor Clarification
1 | Please be noted that there is a buffer tank downstream 20-C-7080 and ultimate goal is to keep the pressure of buffer tank at a constant value. It is worth mentioning that in normal operation the buffer tank has no discharge. This concept is also mentioned in the relevant data sheet. In 20-C-1002 the compressor is in service continuously, there is no need to start/stop automatically. |  |  | The reply is noted, however we will keep the control philosophy the same, since we are using a recycle valve for controlling the pressur. The load/unload (start/stop) pressure would only be used if the is no consumption at all, only for the reason this is required. As we do not want to keep the compressor running in unload conditions for a very long time. we stongly suggest to keep the configuration as is. and check at site if any modification might be required to the software in order to keep it running for most of the time.Based on Airpack experience this is always the best solution CES REPLY: This clarification must be added to CONTROL PHILOSOPHY FOR NITROGEN GAS BOOSTER as a note.
2