## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 31/May/2022 | Rev.:02
|  | Comment Sheet Ref.No.: | Doc Description: UCP/LCP/JB WIRING DIAGRAM FOR EMERGENCY INSTRUMENT AIR COMPRESSOR
|  | Transmittal No.: APCES-V-00137 | Doc. No.: BU-20-VD-303-IN-DIG-0093
|  | Transmittal Date: 31/May/2022 | Doc Rev.: 02
Item | CHCE Comment |  |  | Vendor Clarification |  |  | CES Reply (Nov.04,2021) | CES Reply (Dec.15,2021) | vendor replay (mrt.02 ,2022) | CES Reply (June,14,2022)
1 | - Reply sheet shall be submitted by vendor. - Reference document to be specified. - Prerequisite document such as architecture diagram and I/O list shall be issued before this document. - After FAT minimum of 20 % installed spare in all respects shall be available. - UCP, LCP and JB tag to be modify as per comments on page 2 of P&ID. - Component list BOM same as below table shall be add |  |  | - Noted - Noted - Noted - Noted - Noted - Updated in next revision |  |  | - Closed. - Reference documents are not specified. Updated - Architecture is not issued this shall be send after the wiring diagram - This item will be review after I/O list finalized. noted - Closed. - BOM was not added in the panel laypout all the parts are added and in the wiring diagram the device tag list is added with all components
2 | MARK EXd Please confirm that following specification as per project standard is applicable for cable glands. |  |  | Updated in next revision Exd only for distribution panel Confirmed |  |  | - Closed - With reference to TCL, JBs shall EXD. Airpack comment: BU-20-D-000-IN-DSH-627-03 JUNCTION BOXES AND CABLE GLANDS specification followed no exd jb shall be used only for terminald jb's - Noted for cable gland.
3 | UCP-C7080-01 |  |  | Updated in next revision |  |  | Closed.
4 | EL.03: Use circuit breakers to protect the circuit. if a fault occurs after switches, it might upstream C.B to trip and it's not logical. EL02: Incoming power supply terminal numbers shall be clarified. EL.04: Add a page and show the legend and symbol list. Ventilation system shall be use UPS power supply. |  |  | Circuit breakers are used after the switches for the panel to trip Clarified with text left from terminal block Updated in next revision Ventilation system shall be from NON-UPS as per wiring diagram |  |  | EL03: not accepted. circuit breaker shall be considered in incoming. EL02: Noted. EL04: not accepted. it in not complete and shall be checked and revised. This is included in the wiring diagram it's called the device tag list Ventilation comment is not related to ELEC and shall be replied by INST.
5 | Solenoid valves shall be I.S. with 24 VDC voltage rating. |  |  | Solenoids are NON-IS as per project specification |  |  | Closed.
6 | Modbus TCP/IP shall be considered |  |  | Updated in next revision |  |  | Closed.
7 | 20 % spare to be consider |  |  | Updated in next revision |  |  | This item will be review after I/O list finalized. noted
8 | Solenoid valves shall be I.S. with 24 VDC voltage rating. JIDX-C7080-xx xx=your sequence General comments for JB wiring - Cable type, color and gland size shall be specified and followed same as attached file. - JB and LCP layout shall be added same as attached file. - Entry for multi-pair cables to junction box shall be from bottom. - The minimum degree of protection shall be IP 65. - Terminals shall be certified EEx 'e' (for EEXi and Non EExi signals) in accordance with IEC/CENELEC standards IEC 60079. - The following color codes shall be considered for body of each Junction box: • EEx "e" JB, shall be green (RAL 6021). • EEx "d" JB, shall be gray (RAL 9006). • Each junction box in Intrinsically Safe circuit shall be blue (RAL 5015). - Each box shall have terminal blocks with the following characteristics: • Terminal blocks shall be spring loaded Klippon type and vibration proof • Rating of terminal blocks shall be 600V as minimum • Number of terminals in each junction box shall be 16 or 31 or 41 or 61 - Screens shall be insulated from earth at instrument side. They shall be continuous through to the control room marshaling cabinet where they will be connected to the clean system. |  |  | Solenoids are NON-IS as per project specification, rating is 24VDC Updated in next revision - Updated in next revision - Noted - Confirmed - Confirmed - • Noted • Noted • Noted - • Noted • Noted • Noted - Updated in next revision |  |  | - Closed. - For JB and LCP layout comment please refer to BU-20-VD-303-IN-DWG-0039-01 BU-20-D-000-IN-DSH-627-03 followed - Eex'e' certificate for terminals shall be mentioned as a note and specified in BOM. Noted
9 | Individual and overall screen terminals shall be considered. as per general comment 16 terminal to be consider. |  |  | Updated in next revision |  |  | Closed.
10 | Terminal for overall screen to be consider |  |  | Updated in next revision |  |  | Closed.
11 | - One multi cable is consider for analogue input/output signals, please merge this terminal strip with analogue inputs terminal strip in previous page |  |  | Noted |  |  | Closed.
12 | EL.05: Use circuit breakers to protect the circuit. if a fault occurs after switches, it might upstream C.B to trip and it's not logical. |  |  | Circuit breakers are used after the switch for the panel to trip |  |  | not accepted. ciruit breaker shall be considered for incoming. Circuit breakers for incoming power you need to provide before it's coming inside the panel, inside the panel and for all conponents airpack have included mcb's so after the main switches and before the power converters this is per project specification |  |  | Noted
13 | EL.06: Add following data in the box. From: SWB3A-03(0.4KV) Cable no: EBP-20-C-7080-M Cable Type and Size: CU/XLPE/AWA/PVC3.5*50mm2 Gland: EX-IP66, C2/M40 |  |  | Noted, Updated in next revision |  |  | it is not completed. Refer to coment on document. ( also please note that cable shall be cu/xlpe/swa/pvc, not awa) Updated
14 | EL.07:It's recommended to change the place of Bi-metal and Contactor with each other, EL.08: It shall be 6In EL.09: Specify the CT and Ammeter's data completely. EL.10: Why this contact is used in negative side? Is it standard to connect 24vdc directly to the coil then switch it from negative side? EL.11: Use 3K12 to indicate Running and Stopped position of the motor. (use 2 signal lamps) |  |  | This is the way it should be Updated in next revision This shall be added in the spare part list, this is another document Updated in next revision This are already 2 lamps, 1 for permissive and 1 for fault Updated as per latest P&ID |  |  | EL07: closed. EL08: closed. EL09: not accepted. details shall be added in this drawing beside CT and ammeter symbols. CT added EL10: closed. EL11: emphasized again. This is per P&ID so comment on the P&ID
15 | EL.12: Specify the type and rating of C.B. EL.15: It seems using this aux. relay as Heater Running in this part of the circuit is not sounds suitable, because after that there is a SSR switch and it might be in open status. Please check and clarify. EL.13: Please clarify about the thyristor switch. Add all switch data beside of it, EL.16: Does SSR have any error contact to using in circuit? EL.14: Add all aux. relay's name beside them. EL.17: Is it standard to connect 24vdc directly to the coil then switch it from negative side? Please clarify it. EL.18: Panel layout arrangement shall be prepared and issued. EL.19: Part list shall be added in document. EL.20: Other parts of the wiring document shall be checked by Instrument dep. |  |  | Noted Wiring changed since thermostat is added Wiring changed since thermostat is added Yes inside the UCP panel Yes this is correct Noted Updated in next revision Noted |  |  | EL12: emphasized again. Type shall be added in the spare part list. EL15: it shall be clarified. This is suitable and checked EL13: it shall be clarified. Type shall be added in the spare part list. EL:16: closed. EL14: emphasized again. Updated check all aux references in the wiring diagram for description EL17: closed. EL18,19,20: emphasized again. Part list is added with all information
16 | - Please refer to comments on I/O List, P&ID and other relevant document. - After FAT minimum of 20 % installed spare in all respects shall be available. - Ventilation system (110 V, 50 Hz, UPS) fitted with dust filters and with extraction fans mounted on the top of cabinets shall be provided. - Multi cable for connection pushbuttons and lamps on LCS not specified, please consider one 10Pair cable for LCS signals to UCP and arrange terminal strip accordingly. - PB-71103 on local panel, for compressor ESD PB, I/O card connection is missed. - XS-715 signal and wiring diagram is missed. - Related I/O card for emergency shut down command from ESD to be specified and also ESD command on the UCP panel. - Please modify device tag list in page 8 same as following table : I24 |  |  | - Noted - Noted - fan with filter is included - updated - XS-715? explain - Updated in next revision - noted |  |  |  | - Noted. - Noted. - Panel circulation fan power supply shall be supplied from UPS power supply. - It has not been implemented in the document. - Please refer to your I/O list for description. - It has not been implemented in the document. | - Noted. - Noted. - - It has not been implemented in the document. - Please refer to your I/O list for description. - It has not been implemented in the document.
17 | (RAL 9006) Gray Eex'd' as per TCL shall be selected. IE connection shall be separate to two bar one as ISE for IS signals and the other one as NISE for NIS signals. |  |  | BU-20-D-000-IN-DSH-627-03 JUNCTION BOXES AND CABLE GLANDS specification followed no exd jb shall be used only for terminald jb's BU-20-D-000-IN-DSH-627-03 JUNCTION BOXES AND CABLE GLANDS specification followed no exd jb shall be used only for terminald jb's Exe jb shall be used. ISE shall be added and PE. |  |  |  | - Regarding to vendor deviation to use Ex'd' type solenoid valve so Ex'd' JB with mentioned specification shall be used. Also with reference to TCL, EXd JB shall be used. TCL has highest priority. - Priority of TCL is higher than specification so vendor shall follow agreements on TCL. - It has not been implemented Vendor just change the name of the bar. | -The classification of the solenoid valves has no relation to the classification of the JB. -The colour is changed to Gray RAL9006, as indicated. | - TQ shall be submitted by vendor. - Closed.
18 | EL-03: description shall be specified. |  |  | Updated in next revision. |  |  |  | Closed. | Closed.
19 | FCS |  |  | Updated in next revision. |  |  |  | Closed. | Closed.
20 | EL.01: Use circuit breakers to protect the circuit. if a fault occurs after switches, it might upstream C.B to trip and it's not logical. |  |  | Circuit breakers for incoming power you need to provide before it's coming inside the panel, inside the panel and for all conponents airpack have included mcb's so after the main switches and before the power converters this is per project specification |  |  |  | not accepted. ciruit breaker shall be considered for incoming. | When switching 'on' power supply 2V15 or 2V17 will be turned on. If those are damaged the fuse 2F15 or 2F17 will be deactivated. Same explanation for the other circuit. | Noted
21 | EL02: Incoming power supply terminal numbers shall be clarified. |  |  | Updated in next revision. |  |  |  | Noted | updated in revision.03
22 | - Please clarify to considering display page on the panel door. - As per MR vendor must consider industrial workstation too.I37:N38 |  |  | - display is on panel door - not part of the wiring diagram |  |  |  | - Noted. - Workstation power supply and network connection shall be specified in this document. | not part of the wiring diagram | CLOSE
23 | Tag to be modified |  |  | Updated in next revision. |  |  |  | Closed. | Closed.
24 | ESD |  |  | Updated in next revision. |  |  |  | Closed. | Closed.
25 | EL.08: Add following data in the box. From: SWB3A-03(0.4KV) Cable Type and Size: CU/XLPE/AWA/PVC3.5*50mm2 Gland: EX-IP65, C2/M40 |  |  | Updated in next revision. |  |  |  | Noted | Changed AWA to SWA [closed] | Noted
26 | EL-04: Use circuit breakers to protect the circuit. if a fault occurs after switches, it might upstream C.B to trip and it's not logical. |  |  | This is with MCB protection |  |  |  | Add type of circuit breaker beside related equipment. | When switching 'on' power supply 2V15 or 2V17 will be turned on. If those are damaged the fuse 2F15 or 2F17 will be deactivated. Same explanation for the other circuit. | Noted
27 | EL-05: Single line diagram document shall be revised based on this document. |  |  | Noted |  |  |  | Vendor confirmed. So, closed. | [closed]
28 | EL-07: complete legend sheet shall be added for power distribution panel items. |  |  | Noted |  |  |  | Legend has not been added for power distribution panel items yet. | updated in revision 03 | Noted
29 | EL-06: description shall be added here and in legend. |  |  | Updated in next revision. |  |  |  | There is nothing in this revision. | updated in revision 03 | Noted
30 | EL.09: Specify the CT and Ammeter's data completely. |  |  | Updated in next revision. |  |  |  | There are no changes in comparison to previous revision. | CT is specified in the part-list. Primaire data is added Ammeter's | Noted
31 | EL.10: Use 3K12 to indicate Running and Stopped position of the motor. (use 2 signal lamps) |  |  | This can't be changed since this is per P&ID design |  |  |  | "Running" and "stopped" positions of motor shall be specified with signal lamps. | Running light -> according to Control philosief, UCP XL-71107 and LCP - XL-71102. XL-71112 show status if motor is ready for start. | Not acceptable. Mentioned tags can not be found. "Running" and "stopped" positions of motor shall be specified with signal lamps. There is additional description in the document.
32 | EL.12: Specify the type and rating of C.B. |  |  | Updated in next revision. |  |  |  | There is no changes in comparison to previous revision. | updated in revision 03 | Noted
33 | EL.15: It seems using this aux. relay as Heater Running in this part of the circuit is not sounds suitable, because after that there is a SSR switch and it might be in open status. Please check and clarify. |  |  | This is just a indication for the PLC that the Heater is on. |  |  |  | It seems that this auxiliary relay can not indicate status of heater correctly. Vendor shall confirm that it can show status of heater correctly. | Status will be confirmed correctly. When 4Q3 is de-energized, status will be off. Also no power to the SSR. [Closed] | Vendor confirmed it. Noted
34 | EL.13: Please clarify about the thyristor switch. Add all switch data beside of it, |  |  | Not possible this shall be in the spare part list will be provided later. |  |  |  | All switch data shall be added beside equipment (in this document). | updated in revision 03 | Noted
35 | EL.16: Does SSR have any error contact to using in circuit? |  |  | 4K6 is the Fault contact for the SSR |  |  |  | Noted | 4K6 is changed to 4K12 as per update. [closed]
36 | EL.14: Add all aux. relay's name beside them. |  |  | Description added |  |  |  | Noted | Noted
37 | EL.18: Panel layout arrangement shall be prepared and issued. |  |  | Noted |  |  |  | Noted | Noted
38 | EL.19: Part list shall be added in document. |  |  | Part list is another document the spare part list. |  |  |  | Part list shall be added in document, too. | Noted, and done. See page 7 to 12. [closed] | Noted
38 | EL.20: Other parts of the wiring document shall be checked by Instrument dep. |  |  | Noted |  |  |  | Noted | Noted