## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 16/06/2022 | Rev.: 02
|  | Comment Sheet Ref.No.: | Doc Description: UCP/LCP/JB GENERAL ARRANGEMENT DRAWING & TERMINAL DETAILS FOR EMERGENCY INSTRUMENT AIR COMPRESSOR INCL. BOM
|  | Transmittal No.: APCES-V-00149 | Doc. No.: BU-20-VD-303-IN-DWG-0089
|  | Transmittal Date: 156/06/2022 | Doc Rev.: 02
Item | CHCE Comment |  |  | Vendor Clarification |  |  | CES Reply
1 | dust filter to be added too. |  |  | Updated in next revision CES REPLY: Closed. |  |  | Closed.
2 | tag plate of each panel/JB to be added too. |  |  | Updated in next revision CES REPLY: Closed. |  |  | Closed.
3 | grounding of panel to be added too. 3 separate earth bar shall be considered PE, IS-IE, NIS-IE. |  |  | ISE and PE are included in panel CES REPLY: Please see comments inside document. |  |  | Closed.
4 | to be in accordance with cable sch |  |  | Updated in next revision CES REPLY: Closed. |  |  | Closed.
5 | this page to be moved after page |  |  | Updated in next revision CES REPLY: Closed. |  |  | Closed.
6 | comments on PLC / JBof C-1002 are applicable for C-7080 |  |  | Updated in next revision CES REPLY: Closed. |  |  | Closed.
comments revision 01 below
1 | Modify the MC logo |  |  | Format is the same as the P&ID |  |  | Closed.
2 | EL02: 1- The rear of the door shall be shown with mounted devices and wiring channel. 2-The suitable provision shall be considered for separation of 24Vdc and 230VAC in all trunking and ways. |  |  | Rear side can not be shown this is not part of the panel layout Confirmed separation of 24VDC and 230VAC in all trunking and ways |  |  | 1- Noted 2- Noted
3 | LCP shall be equipped to Ammeter as per TCL |  |  | LCP do not have a Ammeter only on the Distribution panel there is a Ammeter check P&ID |  |  | Noted
4 | EL-03: The terminal Strip code is specified, but terminal numbers shall be add too. |  |  | Updated in next revision |  |  | Noted
5 | EL01: The technical specifications shall be completed in nameplate. The below items shall be added in name plate: -The degree of protection panel -The permissible withstanding short circuit current -The total weight of panel -The insulation voltage of panel -Manufacturer date -The panel tag |  |  | Confirmed |  |  | Vendor confirmed that but any actions have not been done on document.
Rev 03
6 | PE is protective earth for panel earthing, for IS and NIS signals separate earth bar shall be considered. |  |  | Updated in next revision |  |  | Closed.
7 | As per instrument cable list M25 cable gland shall be considered |  |  | Updated in next revision |  |  | Closed.
8 | Required data as per attached file (in previous rev.) was not implemented.(such as name plate, special label and etc.) |  |  | Updated in next revision |  |  | Comment has not been implemented.
9 | According to selecting Eex'd' type solenoid valve, so selected JB shall be Eex'd' too. JB protection shall be considered Eex'd' and its color shall be RAL9006 |  |  | Updated in next revision |  |  | According to your TQ, we accepted that you using Eex 'e' JB, so color of Eex 'e' JB shall be RAL 6021.
10 | According to selecting Eex'd' type solenoid valve, so selected JB shall be Eex'd' too. JB protection shall be considered Eex'd' and its color shall be RAL9006 |  |  | As agreed the junction box remains ex'e , the color of the junction box will be updated in the next revision |  |  | According to your TQ, we accepted that you using Eex 'e' JB, so color of Eex 'e' JB shall be RAL 6021.
11 | Required data as per attached file (in previous rev.) was not implemented.(such as name plate, special label and etc.) |  |  | Already included |  |  | You just specified Tag plate in the document, in addition of it, JB name plate (contain JB technical data) and special lable (contain IS or NIS signals description inside JB as per attached file in rev.1) shall be added to the document.
12 | This is tag plate that you specified, in addition tag plate, name plate and special label (same as attached file in previous rev.) shall be specified in this document. |  |  | Already included |  |  | You just specified Tag plate in the document, in addition of it, JB name plate (contain JB technical data) and special lable (contain IS or NIS signals description inside JB as per attached file in rev.1) shall be added to the document.
13 | Regarding to considering one JB for analogue input/outputs so one terminal strip and one multi cable 10Px0,75 mm² will be considered for this JB, accordingly X2 and X3 shall be merged in to one terminal strip. |  |  | Updated in next revision |  |  | Closed.
14 | To be deleted |  |  | Updated in next revision |  |  | Closed.
15 | This is tag plate that you specified, in addition tag plate, name plate and special label (same as attached file in previous rev.) shall be specified in this document. |  |  | Already included |  |  | You just specified Tag plate in the document, in addition of it, JB name plate (contain JB technical data) and special lable (contain IS or NIS signals description inside JB as per attached file in rev.1) shall be added to the document.
16 | LCP shall be Eex'd' type JB, regarding to NIS signals contain it. accordingly its color shall be RAL9006 |  |  | As agreed the junction box remains ex'e , the color of the junction box will be updated in the next revision |  |  | According to your TQ, we accepted that you using Eex 'e' JB, so color of Eex 'e' JB shall be RAL 6021.
17 | This is tag plate that you specified, in addition tag plate, name plate and special label (same as attached file in previous rev.) shall be specified in this document. |  |  | Already included |  |  | You just specified Tag plate in the document, in addition of it, JB name plate (contain JB technical data) and special lable (contain IS or NIS signals description inside JB as per attached file in rev.1) shall be added to the document.
18 | M25 |  |  | Updated in next revision |  |  | Closed.
19 | EL: Repeated Comment: The technical specifications shall be completed in nameplate. The below items shall be added in name plate: -The degree of protection panel -The permissible withstanding short circuit current -The total weight of panel -The insulation voltage of panel -Manufacturer date -The panel tag |  |  | The data that will be fixed at a later stage, there is a note made on the drawing with the data that will be incorporated into the nameplate as soon as it is known. (note6)dated in next revision |  |  | Closed.