## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 28-07-2022 | Rev.:00
|  | Comment Sheet Ref.No.: | Doc Description: LV DISTRIBUTION PANEL DRAWING FOR NITROGEN GAS BOOSTER
|  | Transmittal No.: APCES-V-00170 | Doc. No.:BU-20-VD-303-EL-DWG-0058
|  | Transmittal Date: 28-07-2022 | Doc Rev.: 00
Item | CHCE Comment |  |  | Vendor Clarification |  |  | CES Reply | Vendor Clarification
1 | Reference drawing shall be added. |  |  | Noted, reference to electrical wiring diagram nitogen gas booster will be added in the next revision. |  |  | Document name shall be added.
2 | comment: 1- SLD & schematic diagram shall be added in next revision . |  |  | Not agreed, the systematic diagram (wiring diagram) shall be provided in a separate document as agreed in the VDS. Reference document: 17811-05A_BU-20-VD-303-IN-DIG-0043_UCP/LCP/JB CONNECTION DIAGRAM FOR STIKSTOFGAS BOOSTER INCL. CRS The same applies to the SLD, this documentation is also supplied separately from this document. Reference document: 17811-049A_BU-20-VD-303-EL-DIG-0049_SINGLE LINE DIAGRAM FOR POWER DISTRIBUTION PANEL FOR NITGROGEN GAS BOOSTER INCL. CRS The reference of both documents will be added in the next revision. |  |  | Noted
| 2- legend for all equipment shall be added. |  |  | The description of all equipment is already included on sheet 1 of this document. Each number on the drawing is related to a description of the equipment. The tagnumer are linked to the wiring diagram. Reference document: 17811-05A_BU-20-VD-303-IN-DIG-0043_UCP/LCP/JB CONNECTION DIAGRAM FOR STIKSTOFGAS BOOSTER INCL. CRS |  |  | Noted
| 3- EU type examination & QAN shall be send. |  |  | This is an airpack supply,the distrution panel is made by us. |  |  | Only technical details will be checked by Eng. Department, and all equipment shall be supplied based on approved sub vendor list. So, this item in closed.
3 | each equipment shall be clarify? |  |  | Has already been described, see sheet 1 of the document. |  |  | Noted
4 | copper free cast aluminium |  |  | Noted, will be updated in the next revision. |  |  | Noted
5 | Color shall be rechecked. |  |  | Noted, will be updated in the next revision. |  |  | Noted
3 | Modify the MC logo |  |  | Noted, will be updated in the next revision.
4 | BU-20-VD-303-EL-DWG-0058 |  |  | Noted, will be updated in the next revision.
5 | 1 |  |  | Noted, will be updated in the next revision.
5 | P |  |  | Noted, will be updated in the next revision.