## COMMENT REPLY SHEET
|  | Comment Reply Sheet |  |  | BUSHEHR PETROCHEMICAL COMPANY
Con. No.:
[5 empty] | Issue Date: 03/Nov/2022 | Rev.:08
|  | Comment Sheet Ref.No.: | Doc Description: Instrument Datasheets for Nitrogen gas booster
|  | Transmittal No.: APCES-V-00192 | Doc. No.: BU-20-VD-303-IN-DSH-0040
|  | Transmittal Date: 03/Nov/2022 | Doc Rev.: 08
Item | CHCE Comment |  |  | Vendor Clarification |  |  | CES Reply | Vendor Clarification (2) | CES Reply (2) | Vendor Clarification (3) | CES Reply (3) | Vendor Clarification (4) | CES Reply (4)
1 | P&ID number to be modified as per related P&ID document number for all instruments. |  |  | Updated in next revision |  |  | Closed.
2 | General comment for all PG/PDG gauges shall be provided with zero stop pin and zero adjustable mechanis, shall be provided. |  |  | Updated in next revision |  |  | Closed.
3 | As per project specification PDG connection shall be 1/2" NPT |  |  | For PDG 1/4" is standard connection, 1/2" not available. Airpack will supply 1/4"/ 1/2" connectors. |  |  | Closed.
4 | 0-25 standard range to be considered |  |  | Updated in next revision |  |  | Closed.
5 | Bar (g) |  |  | All other pressures in process and scales are indicated with bar(a) |  |  | Closed.
4 | Gauges with maximum scale value of 25 bar g and more shall be solid front |  |  | Updated in next revision |  |  | Closed.
5 | Please be informed that pipe to be expanded to 4" for installation of TW on pipe |  |  | Noted, however line number as per P&ID. |  |  | Closed.
6 | Stem orientation shall be every angle. |  |  | This is for fieldmounted gauges, not fpr panel mounted. |  |  | Closed.
7 | 10004/ 10002; based on based on vendor PID |  |  | Not clear what you mean please clarify. |  |  | Closed.
8 | U-length shall be specified by Airpack so that with considering TW tip stai on the middle third of pipe. |  |  | Updated in next revision |  |  | Please specify TW nozzle projection. it seems that selected U-length is too short to TW tip stay on the middle third of pipe. | It is double checked and we confim TW-tip stay on th middel third of pipe. | Closed. It is in vendor responsibility to supply suficant TW length based on project requirements.
9 | XY-71102 is missed |  |  | This tag is not mentioned in the P&ID. |  |  | Closed.
10 | XY-10002 is one of the XV-10002 accessories it shall be removed and mentioned in On-off valve datasheet. |  |  | As it has a separate Tag number a seperated dataheet has been incorporated and not only an accessorie of valves. |  |  | Solenoid valve shall has a separate tag no. but it is one of the XV-10002 accessories and must be mentioned in on-off valve data sheet and removed from this data sheet. | Cross reference will be made on the XV-10002 datasheet referinge to the XY-10002 datasheet | Closed.
11 | - Please issue this document after P&ID approval and received sub-vendor complete information. |  |  | P&ID has been updated, inquiries for instruments are sent after approval of drawings, only af that the fnal information will be submitted. So please first approve the items as they are now so we can sent inquiries to our sub-vendors. |  |  | Updated P&ID has not been issued yet, latest revision of P&ID (rev.1) has not conformity with instrument data sheet. Noted, instrument MFR and model must be specified after data sheet approval. | P&ID rev.02 has been issued 3/11/2021. | Closed.
12 | - Manufacturer and Model no. for all items must be specified. |  |  | see reply Item 11 |  |  | See reply Item 11 |  | Specifying MFR. and model no is not related to P&ID, regarding to data sheet was approved as note you must specify mentioned items.
13 | - All "VTA" and "To be advised by supplier" and etc. to be specified in next rev. |  |  | see reply Item 11 |  |  | See reply Item 11 |  | See reply item 12.
14 | Document shall be updated based on comments on P&ID |  |  | Updated in next revision |  |  | Closed.
15 | 85 oC.the comment is valid for other instruments on the line. |  |  | Updated in next revision |  |  | Closed.
16 | Based on PID the operating temperature of the inter cooler is 180 oC while the normal and Max. temperature of the relevant instruments do not cover it. This comment is valid for other related document such as PSV Data Sheet. |  |  | 180° C is not mentioned on the PID |  |  |  | O.T is 134°C as per P&ID | Closed.
17 | 100 oC.Must be consider for all cooling water lines |  |  | 95°C as per PID will be updated in next revision. |  |  | Not accepted. The comment must be taken into consideration. | D.T is 95°C as per P&ID | Closed.
18 | 7 barg. Must be consider for all cooling water lines. |  |  | 10 barg as per PID will be updated in next revision. |  |  | Not accepted. The comment must be taken into consideration. | D.P is 10 barg as per P&ID | Closed.
19
19 | G.N 1. Any nodification must be highlighted. |  |  | Modifications highlighted in red. |  |  |  |  | Closed.
20 | G.N 2. All documents must be consistent with each other in terms of tag.numbers, line numbers and so on. |  |  | Updated in next revision |  |  |  |  | Closed.
21 | G.N 3. It is not clear why tag numbers are being changed, yet this document will be finalized when PID is issued. |  |  | Tagnumbers as per P&ID. |  |  |  |  | Closed.
22 | PG-10161 |  |  | Updated in next revision |  |  |  |  | Closed.
23 | Gauge savers shall be considered for the services such that full scale of the gauge is smaller than its design pressure. |  |  | Full scale range will be updated in next revision. |  |  |  |  | Closed.
24 | Repeated comment; Airpack shall submit Wake Frequency calculation sheets to meet ASME PTC 19.3 to purchaser for approval. |  |  | Calculations are not part of the agreed scope of supply. |  |  |  |  | According to signed MRQ by Airpack, section RFD, page 26, clause TE97 "Stress analysis and Calculation for thermowell" shall be supplied by Airpack.(your temp. element sub-vendor must submit wake frequency calculation)
25
25 | Manufacturer and model no. must be specified after data sheet approval or approved as note. also "VTA" , "To be advised by supplier" and etc. must be specified too. |  |  | Updated in next revision "AFC" after purchase. |  |  | Noted, also in page 32 of 34 for FT-10151 low alarm shall be modify to 13 m3/hr. | Updated in next revision | Noted.
25 | Repeated comment; Airpack shall submit Wake Frequency calculation sheets to meet ASME PTC 19.3 to purchaser for approval. |  |  | According to signed MRQ by Airpack, section RFD, page 26, clause TE97 "Stress analysis and Calculation for thermowell" shall be supplied by Airpack.(your temp. element sub-vendor must submit wake frequency calculation), however it is only mentioned if applicable, and it is not menioned in the specifcation if it is applicable. therefore it has not been considered |  |  | Wake frequency calculation is applicable for thermowells, and also as per ESS for Package Instrumentation 1216-DE-00-IN-ESS-603 page 48 of 75 "The design of the thermowells shall be verified for all items by vendor by means of stress analysis, resulting from stream velocity condition. Frequency limitation shall meet ASME PTC 19.3 TW-2010. Vendor shall submit the calculation sheets to purchaser for approval." Similar to other packages in this project, Airpack must submitted wake frequency calculation. | Please refer to MR, we can offer it against extra costs | Wake frequency calculation is a part of your contract as per mentioned in previous reply and you are not specify it as a deviation in your deviation list, so you must submit calculation and also extra cost is not accepted for this issue. Please specify fluid velocity in the data sheet | again it is not a deviation, since it is not specified in your datasheets. In the MR it is mentioned that if it is applicable, however it is not menioned that it is applicable and therefor it is not considered a deviation. We will only do this against extra cost, since it is not calculated in our offer. | As per previous reply, vendor shall specify fluid velocity in data sheet. After that we will check it, if velocity is suitable, calculation is not required. but if it is critical, calculations shall be submitted by vendor. | Velocitys are calculated as follows: TG-10156: 0,9 m/s TG-10157/58: 0,4 m/s TIT-10151: 2,6 m/s TIT-1052/53: 1,9 m/s TIT-10154/55: 1,4 m/s | Noted, With considering that wake frequency calculation has not been submitted by vendor so following dimensions of thermowell shall be specified in TW data sheet : • Root diameter • Tip diameter • Tip thickness • Bore diameter • Nozzle projection
25 | [8 empty] | Data sheet and calculation sheet for FO-10151~54 that recently added in P&ID shall be bring in the data sheet. (please refer to attached file for sample format of FO data sheet) | Updated in next revision | Noted. |  | Data sheet for FO-10154 is missed. Some data are missed in orifice plate data sheet, please follow attached file.
25
25 | - Data sheet for FO-10154 is missed. |  |  | Noted will be added
25 | Discrepancy with instrument index please clarify. |  |  | is updated for next revision of the index
25 | 1. Discrepancy with mechanical data sheet. In data sheet 14.5 bara |  |  | Noted and updated
25 | Selected range shall be in standard range.(0~25) |  |  | range cannot be changed anymore, order has been done.
25 | 2. 52 oC |  |  | Noted and updated
25 | 3. 2" |  |  | Noted and updated
25 | 1. Discrepancy with mechanical data sheet. In data sheet 14.5 bara |  |  | Noted and updated
25 | With considering that wake frequency calculation has not been submitted by vendor so following dimensions of thermowell shall be specified in TW data sheet : • Root diameter • Tip diameter • Tip thickness • Bore diameter • Nozzle projection |  |  | Noted and updated
25 | To be specified |  |  | Noted and updated
25 | Comments in this page are applicable for other Thermowell too. |  |  | Noted and updated
25 | Manufacture and model no. shall be specified |  |  | Noted and updated
25 | 1. Discrepancy with mechanical data sheet. In data sheet 14.5 bara |  |  | Noted and updated
25 | 7. Discrepancy. Based on Data sheet 64 oC |  |  | Noted and updated
25 | 8. Discrepancy. Shall be finalized based on comment on PID |  |  | Noted and updated
25 | Orifice data sheet is not complete some data such as follow must be added (also you can use attached FO data sheet to the reply sheet) : • Sizing standard (ISO 5167) • Type of bore (Concentric square edge or etc.) • Orifice bore diameter • Beta ratio • Plate thickness • Plate material |  |  | Noted and updated
26 | Wall thickness is thinner than dimensional Limits listed in ASME PTC 19.3 TW-2010 Tables 4-1-1 or 4-2-1 |  |  | specification only mentiones ASME PTC 19.3 TW-2010 Tables 4-1-1 or 4-2-1 for calculation, since this was not included. This is not followed. Also if you insist, it will be against extra cost, since this comment was given late thermowells haven already been menufactured |  |  | This is deviation from standard ASME PTC 19.3 and regarding that vendor has not been submitted calculation sheet for wake frequency so it is not accepted and client must make a decision about this issue. | thermowells have been ordered already not changes are possible anymore | Wake frequency calculation was our requirement from the first revision of data sheet, but we ignored this issue for the urgency of the project, considering that the vendor deviates from ASME PTC19.3 standard and also wake frequency calculation has not been submitted by vendor, this issue is not accepted and client must make a decision about this issue. You should guarantee your design and submit TQ for client approval. | we will not submit a TQ, this was no included in our offer as I have mentioned several times. There is no use in discussing this further. The materials are order and have arived in our workshop and are installed. The specifation only show that we have to do it if it is mentioned in the dataheets. which it wasn't we are following the specification. please approve the next revision of the document to prevent any further delay | I know that you have already purchase the instrumentation for both compressors. However, TQ is required for guarantee of your design. Without TQ, document will not approve.
27 | Root diameter shall be 25 mm Tip diameter shall be 19 mm Tip thickness shall be 6.4 mm Bore diameter shall be 6.6 mm |  |  | specification only mentiones ASME PTC 19.3 TW-2010 Tables 4-1-1 or 4-2-1 for calculation, since this was not included. This is not followed. Also if you insist, it will be against extra cost, since this comment was given late thermowells haven already been menufactured |  |  | This is deviation from standard ASME PTC 19.3 and regarding that vendor has not been submitted calculation sheet for wake frequency so it is not accepted and client must make a decision about this issue. | thermowells have been ordered already not changes are possible anymore | Wake frequency calculation was our requirement from the first revision of data sheet, but we ignored this issue for the urgency of the project, considering that the vendor deviates from ASME PTC19.3 standard and also wake frequency calculation has not been submitted by vendor, this issue is not accepted and client must make a decision about this issue. You should guarantee your design and submit TQ for client approval. | we will not submit a TQ, this was no included in our offer as I have mentioned several times. There is no use in discussing this further. The materials are order and have arived in our workshop and are installed. The specifation only show that we have to do it if it is mentioned in the dataheets. which it wasn't we are following the specification. please approve the next revision of the document to prevent any further delay | I know that you have already purchase the instrumentation for both compressors. However, TQ is required for guarantee of your design. Without TQ, document will not approve.
28 | due to the nozzle projection and U-length, thermowell will not fitted in its place, accordingly nozzle projection shall be modified so that thermowell properly fitted and also tips of thermowell to be in the middle third of pipe. |  |  | Nozzle projection110 mm will be updated |  |  | Closed.
29 | Comments in this page are applicable for other Thermowell too. |  |  | Noted and updated |  |  | Closed.
30 | Line size to be specified |  |  | Noted and updated |  |  | Closed.
31 | As per project specification "Orifice bores shall be calculated by using the formula based on ISO 5167." |  |  | this is not the case in the orrifice, the calculaton comes from API 618 pulsation study, therefore calculation will not be done in ISO 5167 |  |  | Closed.
32 | Material shall be specified with ASTM code |  |  | ASTM A694 F52 will be updated. |  |  | Closed.
33 | Comments in this page are applicable for other FO. |  |  | Noted and updated |  |  | Closed.
34
35