## ASPC
ELECTRICAL LOAD LIST
No. | Item No. | Description |  | Q'ty | Operation Mode |  |  | Emergency Supply | Voltage | Phase | Freq | Rated Power | Shaft Power | Effic'y | PF | Remarks
[5 empty] | C | I | S | O/X | [V] | 1/3 | [hz] | [kW] | [kW] | [%] | [%]
Conveying Station / Rotary Valve
1 | 44Z-50001A/B | Conveying Station (18") |  | 2 | 1 |  | 1 | X | 400 | 3 | 50 | 5.5 | 4.4 | - | - | ASD
2 | 44Z-80001A~F | Conveying Station (18") |  | 6 | 6 |  |  | X | 400 | 3 | 50 | 5.5 | 4.4 | - | - | ASD
3 | 44Z-80002A~F | Conveying Station (18") |  | 6 | 6 |  |  | X | 400 | 3 | 50 | 5.5 | 4.4 | - | - | ASD
4 | 44Z-80005A/B | Rotary Valve (18") |  | 2 | 2 |  |  | X | 400 | 3 | 50 | 3.75 | 2.25 | - | - | ASD
5 | 44Z-800011/12/13 | Rotary Valve (10") |  | 3 | 3 |  |  | X | 400 | 3 | 50 | 0.75 | 0.45 | - | -
Compressor
6 | 44C-80001A/B | Compressor Main Drive Motor |  | 2 | 2 |  |  | X | 6000 | 3 | 50 | Later | Later | - | -
7 |  | Space Heater for Main Motor |  | 2 | 2 |  |  | X | 230 | 1 | 50 | Later | Later | - | -
8 |  | Fluff Transfer Compressor LCP | UPS Power | 2 | 2 |  |  | X | 230 | 1 | 50 | Later | Later | - | -
9 |  |  | Normal Power | 2 | 2 |  |  | X | 230 | 1 | 50 | Later | Later | - | - | Normal power includes Canopy Heaters, etc
10 |  | Oil Pump |  | 2 | 2 |  |  | X | 400 | 3 | 50 | Later | Later | - | -
11 | 44C-80002A/B | Compressor Main Drive Motor |  | 2 | 2 |  |  | X | 6000 | 3 | 50 | Later | Later | - | -
12 |  | Space Heater for Main Motor |  | 2 | 2 |  |  | X | 230 | 1 | 50 | Later | Later | - | -
13 |  | Fluff Transfer Compressor LCP | UPS Power | 2 | 2 |  |  | X | 230 | 1 | 50 | Later | Later | - | -
14 |  |  | Normal Power | 2 | 2 |  |  | X | 230 | 1 | 50 | Later | Later | - | - | Normal power includes Canopy Heaters, etc
15 |  | Oil Pump |  | 2 | 2 |  |  | X | 400 | 3 | 50 | Later | Later | - | -
16 | 44C-80004A/B | Compressor Main Drive Motor |  | 2 | 2 |  |  | X | 6000 | 3 | 50 | Later | Later | - | -
17 |  | Space Heater for Main Motor |  | 2 | 2 |  |  | X | 230 | 1 | 50 | Later | Later | - | -
18 |  | Fluff Transfer Compressor LCP | UPS Power | 2 | 2 |  |  | X | 230 | 1 | 50 | Later | Later | - | -
19 |  |  | Normal Power | 2 | 2 |  |  | X | 230 | 1 | 50 | Later | Later | - | - | Normal power includes Canopy Heaters, etc
20 |  | Oil Pump |  | 2 | 2 |  |  | X | 400 | 3 | 50 | Later | Later | - | -
21 | 44C-80005A/B/C | Compressor Main Drive Motor |  | 3 | 2 |  | 1 | X | 6000 | 3 | 50 | Later | Later | - | -
22 |  | Space Heater for Main Motor |  | 3 | 2 |  | 1 | X | 230 | 1 | 50 | Later | Later | - | -
23 |  | Fluff Transfer Compressor LCP | UPS Power | 3 | 2 |  | 1 | X | 230 | 1 | 50 | Later | Later | - | -
24 |  |  | Normal Power | 3 | 2 |  | 1 | X | 230 | 1 | 50 | Later | Later | - | - | Normal power includes Canopy Heaters, etc
25 |  | Oil Pump |  | 3 | 2 |  | 1 | X | 400 | 3 | 50 | Later | Later | - | -
26 | 44C-80006A/B | Elutriator Fan |  | 2 | 1 |  | 1 | X | 400 | 3 | 50 | 30 | 22.7 | - | -
Note ; | 1. Legend ; C : Continuous, I : Intermittent, S : Stand-by

## Sample2
ELECTRICAL LOAD LIST
No. | Unit | Item No. | Description | Q'ty | Operation Mode |  |  | Load Type | Emergency Supply | Voltage | Phase | Freq | Rated Power | Shaft Power | Effic'y | PF | Remarks
| (Note 5) |  |  |  | C | I | S | M/H/O (Note 6) | O/X (Note 7) | [V] | 1/3 | [hz] | [kW/kVA] (Note 3) | [kW/kVA] (Note 4) | [%] | [%]
|  | <K-8410 A/B> | <Chilled Water Generation A/B> | [14 empty] | Voltage (Project Specification) | 13200
| 20 | KM-8410 A/B | Motor for Main Compressor | 2 | 1 |  | 1 | M | X | 4000 | 3 | 60 | 1350 kW | 1161 kW |  |  |  |  | 4000
| 20 | PM-8410 A/B | Motor for Lube Oil Pump of Compressor | 2 | 1 |  | 1 | M | O | 460 | 3 | 60 | 7.5 kW | 5.8 kW |  |  |  |  | 460
| 20 | PM-8411 A/B | Motor for Lube Oil Pump of Main Motor | 2 | 1 |  | 1 | M | O | 460 | 3 | 60 | 0.75 kW | 0.2 kW |  |  |  |  | 220
| 20 | BM-8410 A/B | Motor for Ventilation Fan | 2 | 1 |  | 1 | M | X | 460 | 3 | 60 | 0.75 kW | 0.2 kW |  |  |  |  | 120
| 20 | E-8410 | Oil Heater for Lube Oil System of Comp | 1 | 1 |  |  | H | X | 120 | 1 | 60 | 6 kVA |  |  |  |  | Exception (Fill after informed by Vendor)
| 20 | E-8411 | Oil Heater for Lube Oil System of Motor | 1 | 1 |  |  | H | X | 120 | 1 | 60 | 1 kVA
| 20 | E-8411 A/B | Space heater for Motor | 2 | 2 |  |  | H | X | 120 | 1 | 60 | 0.4 kVA
Note ; |  | 1. Legend ; C : Continuous, I : Intermittent, S : Stand-by
2. All Electrical Consumers shall be listed on this format including Auxiliary Loads such as Lube Oil Pump, Electrical Heater, Control Panel, Space Heater, Stroke Controller and etc.
3. Rated kW : Motor Name Plate Rating or kVA Rating of the load (Rated kW or kVA per one(1) load)
4. Shaft kW : Mechanical Power Input to Driven Shaft to Obtain Rated Output from Driving Equipment or Absorbed Electrical Power for Non-Motor Loads
5. Unit No. : 20 / 21
6. Load Type : M (Motor) or H (Heater) or O (Others) depending on the type of load.
7. Emergency Supply : Vendor shall denote X (Normal) or O (Emergency) depending on Power Supply Requirement. (If power interruption is not allowed)
※ No part of this document may be circulated, quoted, or reproduced without prior written approval from Daelim. ※ 이 정보(문서)는 대림산업㈜의 자산으로서, 허가 없는 사외반출을 금지합니다.
REFERENCE ONLY
Note on K8: Voltage shall be selected by vendor per project specification.
Note on K9: Voltage shall be selected by vendor per project specification.
Note on K10: Voltage shall be selected by vendor per project specification.
Note on K11: Voltage shall be selected by vendor per project specification.
Note on K12: Voltage shall be selected by vendor per project specification.
Note on K13: Voltage shall be selected by vendor per project specification.
Note on K14: Voltage shall be selected by vendor per project specification.
Note on K15: Voltage shall be selected by vendor per project specification.
Note on K16: Voltage shall be selected by vendor per project specification.
Note on K17: Voltage shall be selected by vendor per project specification.
Note on K18: Voltage shall be selected by vendor per project specification.
Note on K19: Voltage shall be selected by vendor per project specification.
Note on K20: Voltage shall be selected by vendor per project specification.
Note on K21: Voltage shall be selected by vendor per project specification.
Note on K22: Voltage shall be selected by vendor per project specification.
Note on K23: Voltage shall be selected by vendor per project specification.
Note on K24: Voltage shall be selected by vendor per project specification.
Note on K25: Voltage shall be selected by vendor per project specification.
Note on K26: Voltage shall be selected by vendor per project specification.
Note on K27: Voltage shall be selected by vendor per project specification.

## 참고
ELECTRICAL LOAD LIST
No. | Unit | Item No. | Description |  | Q'ty | Operation Mode |  |  | Load Type | Emergency Supply | Voltage | Phase | Freq | Rated Power | Shaft Power | Effic'y | PF | Remarks
| (Note 5) |  |  |  |  | C | I | S | M/H/O (Note 6) | O/X (Note 7) | [V] | 1/3 | [hz] | [HP/kW] (Note 3) | [HP/kW] (Note 4) | [%] | [%]
Rotary Valve
1 | 20 | Y-5001 | Purge Cloumn Rotary Valve (30") |  | 1 | 1 |  |  | M | X | 460 | 3 | 60 | 30 / 22 |  |  |  | ASD
2 | 20 | Y-6003 | Fluff Silo Rotary Valve (20") |  | 1 | 1 |  |  | M | X | 460 | 3 | 60 | 10 / 7.5 |  |  |  | ASD
3 | 20 | - | Electric Heat Tracing for Rotary Feeder(Y-5001) |  | - |  |  |  | H | X | 120 | 1 | 60 | 3.54 / 2.64 |  |  |  |  | 케이시스텍 견적서 적용 (06/22 2:29메일 수신)
4 | 20 | - | Electric Heat Tracing for Rotary Feeder(Y-6003) |  | - |  |  |  | H | X | 120 | 1 | 60 | 1.91 / 1.42 |  |  |  |  | 케이시스텍 견적서 적용 (06/22 2:29메일 수신)
Compressor
5 | 20 | C-6004A | Fluff Transfer Compressor Main Drive Motor |  | 1 | 1 |  |  | M | X | 4000 | 3 | 60 | 500 / 375
6 |  |  | Space Heater for Main Motor |  | 1 | 1 |  |  | H | X | 120 | 1 | 60 | 0.47 / 0.36
7 |  |  | Fluff Transfer Compressor LCP (20-PECS-CAB-33A) | UPS Power | 1 | 1 |  |  | O | X | 120 | 1 | 60 | 0.7 / 0.5
8 |  |  |  | Normal Power | 1 | 1 |  |  | M,H | X | 120 | 1 | 60 | 6.13 / 3.8 |  |  |  | Normal power includes Canopy Heaters, etc
9 | 20 | C-6004B | Fluff Transfer Compressor Main Drive Motor |  | 1 | 1 |  |  | M | X | 4000 | 3 | 60 | 500 / 375
10 |  |  | Space Heater for Main Motor |  | 1 | 1 |  |  | H | X | 120 | 1 | 60 | 0.47 / 0.36
11 |  |  | Fluff Transfer Compressor LCP (20-PECS-CAB-33B) | UPS Power | 1 | 1 |  |  | O | X | 120 | 1 | 60 | 0.7 / 0.5
12 |  |  |  | Normal Power | 1 | 1 |  |  | M,H | X | 120 | 1 | 60 | 6.13 / 3.8 |  |  |  | Normal power includes Canopy Heaters, etc
13 | 20 | C-6004C | Fluff Transfer Compressor Main Drive Motor |  | 1 | 1 |  |  | M | X | 4000 | 3 | 60 | 500 / 375
14 |  |  | Space Heater for Main Motor |  | 1 | 1 |  |  | H | X | 120 | 1 | 60 | 0.47 / 0.36
15 |  |  | Fluff Transfer Compressor LCP (20-PECS-CAB-33C) | UPS Power | 1 | 1 |  |  | O | X | 120 | 1 | 60 | 0.7 / 0.5
16 |  |  |  | Normal Power | 1 | 1 |  |  | M,H | X | 120 | 1 | 60 | 6.13 / 3.8 |  |  |  | Normal power includes Canopy Heaters, etc
Utility Power
17 | 20 | 20-PECS-CAB-33 | PLC Control Panel (UPS Power) |  | 1 | 1 |  |  | O | X | 120 | 1 | 60 | 1.4 / 1.0 |  |  |  | For Control Circuit
18 |  |  | PLC Control Panel (AC Clean Power) |  | 1 | 1 |  |  | O | X | 120 | 1 | 60 | 1.4 / 1.0 |  |  |  | For Control Circuit
19 |  |  | PLC Control Panel (Normal Power) |  | 1 | 1 |  |  | O | X | 120 | 1 | 60 | 0.27 / 0.2 |  |  |  | For Space Heater and Lighting
Note ; |  | 1. Legend ; C : Continuous, I : Intermittent, S : Stand-by
2. All Electrical Consumers shall be listed on this format including Auxiliary Loads such as Lube Oil Pump, Electrical Heater, Control Panel, Space Heater, Stroke Controller and etc.
3. Rated kW : Motor Name Plate Rating or kVA Rating of the load (Rated kW or kVA per one(1) load)
4. Shaft kW : Mechanical Power Input to Driven Shaft to Obtain Rated Output from Driving Equipment or Absorbed Electrical Power for Non-Motor Loads
5. Unit No. : 20 / 21
6. Load Type : M (Motor) or H (Heater) or O (Others) depending on the type of load.
7. Emergency Supply : Vendor shall denote X (Normal) or O (Emergency) depending on Power Supply Requirement. (If power interruption is not allowed)
Rotary Valve
1 | 21 | Y-5001 | Purge Cloumn Rotary Valve (30") |  | 1 | 1 |  |  | M | X | 460 | 3 | 60 | 30 / 22 |  |  |  | ASD
2 | 21 | Y-6003 | Fluff Silo Rotary Valve (20") |  | 1 | 1 |  |  | M | X | 460 | 3 | 60 | 10 / 7.5 |  |  |  | ASD
3 | 21 | - | Electric Heat Tracing for Rotary Feeder(Y-5001) |  | - |  |  |  | H | X | 120 | 1 | 60 | 3.54 / 2.64
4 | 21 | - | Electric Heat Tracing for Rotary Feeder(Y-6003) |  | - |  |  |  | H | X | 120 | 1 | 60 | 1.91 / 1.42
Compressor
5 | 21 | C-6004A | Fluff Transfer Compressor Main Drive Motor |  | 1 | 1 |  |  | M | X | 4000 | 3 | 60 | 500 / 375 | [5 empty] | Exception (Fill after informed by Vendor)
6 |  |  | Space Heater for Main Motor |  | 1 | 1 |  |  | H | X | 120 | 1 | 60 | 0.47 / 0.36
7 |  |  | Fluff Transfer Compressor LCP (21-PECS-CAB-33A) | UPS Power | 1 | 1 |  |  | O | X | 120 | 1 | 60 | 0.7 / 0.5
8 |  |  |  | Normal Power | 1 | 1 |  |  | M,H | X | 120 | 1 | 60 | 6.13 / 3.8 |  |  |  | Normal power includes Canopy Heaters, etc
9 | 21 | C-6004B | Fluff Transfer Compressor Main Drive Motor |  | 1 | 1 |  |  | M | X | 4000 | 3 | 60 | 500 / 375
10 |  |  | Space Heater for Main Motor |  | 1 | 1 |  |  | H | X | 120 | 1 | 60 | 0.47 / 0.36
11 |  |  | Fluff Transfer Compressor LCP (21-PECS-CAB-33B) | UPS Power | 1 | 1 |  |  | O | X | 120 | 1 | 60 | 0.7 / 0.5
12 |  |  |  | Normal Power | 1 | 1 |  |  | M,H | X | 120 | 1 | 60 | 6.13 / 3.8 |  |  |  | Normal power includes Canopy Heaters, etc
13 | 21 | C-6004C | Fluff Transfer Compressor Main Drive Motor |  | 1 | 1 |  |  | M | X | 4000 | 3 | 60 | 500 / 375
14 |  |  | Space Heater for Main Motor |  | 1 | 1 |  |  | H | X | 120 | 1 | 60 | 0.47 / 0.36
15 |  |  | Fluff Transfer Compressor LCP (21-PECS-CAB-33C) | UPS Power | 1 | 1 |  |  | O | X | 120 | 1 | 60 | 0.7 / 0.5
16 |  |  |  | Normal Power | 1 | 1 |  |  | M,H | X | 120 | 1 | 60 | 6.13 / 3.8 |  |  |  | Normal power includes Canopy Heaters, etc
Utility Power
17 | 21 | 21-PECS-CAB-33 | PLC Control Panel (UPS Power) |  | 1 | 1 |  |  | O | X | 120 | 1 | 60 | 1.4 / 1.0 |  |  |  | For Control Circuit
18 |  |  | PLC Control Panel (AC Clean Power) |  | 1 | 1 |  |  | O | X | 120 | 1 | 60 | 1.4 / 1.0 |  |  |  | For Control Circuit
19 |  |  | PLC Control Panel (Normal Power) |  | 1 | 1 |  |  | O | X | 120 | 1 | 60 | 0.27 / 0.2 |  |  |  | For Space Heater and Lighting
Note ; |  | 1. Legend ; C : Continuous, I : Intermittent, S : Stand-by
2. All Electrical Consumers shall be listed on this format including Auxiliary Loads such as Lube Oil Pump, Electrical Heater, Control Panel, Space Heater, Stroke Controller and etc.
3. Rated kW : Motor Name Plate Rating or kVA Rating of the load (Rated kW or kVA per one(1) load)
4. Shaft kW : Mechanical Power Input to Driven Shaft to Obtain Rated Output from Driving Equipment or Absorbed Electrical Power for Non-Motor Loads
5. Unit No. : 20 / 21
6. Load Type : M (Motor) or H (Heater) or O (Others) depending on the type of load.
7. Emergency Supply : Vendor shall denote X (Normal) or O (Emergency) depending on Power Supply Requirement. (If power interruption is not allowed)
Note ; |  | 1. Legend ; C : Continuous, I : Intermittent, S : Stand-by
2. All Electrical Consumers shall be listed on this format including Auxiliary Loads such as Lube Oil Pump, Electrical Heater, Control Panel, Space Heater, Stroke Controller and etc.
3. Rated kW : Motor Name Plate Rating or kVA Rating of the load (Rated kW or kVA per one(1) load)
4. Shaft kW : Mechanical Power Input to Driven Shaft to Obtain Rated Output from Driving Equipment or Absorbed Electrical Power for Non-Motor Loads
5. Unit No. : 20 / 21
6. Load Type : M (Motor) or H (Heater) or O (Others) depending on the type of load.
7. Emergency Supply : Vendor shall denote X (Normal) or O (Emergency) depending on Power Supply Requirement. (If power interruption is not allowed)
※ No part of this document may be circulated, quoted, or reproduced without prior written approval from Daelim. ※ 이 정보(문서)는 대림산업㈜의 자산으로서, 허가 없는 사외반출을 금지합니다.
Note on L9: Voltage shall be selected by vendor per project specification.
Note on L10: Voltage shall be selected by vendor per project specification.
Note on L15: Voltage shall be selected by vendor per project specification.
Note on L19: Voltage shall be selected by vendor per project specification.
Note on L23: Voltage shall be selected by vendor per project specification.
Note on L48: Voltage shall be selected by vendor per project specification.
Note on L49: Voltage shall be selected by vendor per project specification.
Note on L54: Voltage shall be selected by vendor per project specification.
Note on L58: Voltage shall be selected by vendor per project specification.
Note on L62: Voltage shall be selected by vendor per project specification.
Note on L86: Voltage shall be selected by vendor per project specification.
Note on L87: Voltage shall be selected by vendor per project specification.
Note on L88: Voltage shall be selected by vendor per project specification.
Note on L89: Voltage shall be selected by vendor per project specification.
Note on L90: Voltage shall be selected by vendor per project specification.
Note on L91: Voltage shall be selected by vendor per project specification.
Note on L92: Voltage shall be selected by vendor per project specification.
Note on L93: Voltage shall be selected by vendor per project specification.
Note on L94: Voltage shall be selected by vendor per project specification.
Note on L95: Voltage shall be selected by vendor per project specification.
Note on L96: Voltage shall be selected by vendor per project specification.
Note on L97: Voltage shall be selected by vendor per project specification.
Note on L98: Voltage shall be selected by vendor per project specification.
Note on L99: Voltage shall be selected by vendor per project specification.
Note on L100: Voltage shall be selected by vendor per project specification.
Note on L101: Voltage shall be selected by vendor per project specification.
Note on L102: Voltage shall be selected by vendor per project specification.
Note on L103: Voltage shall be selected by vendor per project specification.
Note on L104: Voltage shall be selected by vendor per project specification.
Note on L105: Voltage shall be selected by vendor per project specification.
Note on L106: Voltage shall be selected by vendor per project specification.
Note on L107: Voltage shall be selected by vendor per project specification.
Note on L108: Voltage shall be selected by vendor per project specification.
Note on L109: Voltage shall be selected by vendor per project specification.
Note on L110: Voltage shall be selected by vendor per project specification.
Note on L111: Voltage shall be selected by vendor per project specification.
Note on L112: Voltage shall be selected by vendor per project specification.