## ASPC
UTILITY CONSUMPTION LIST
No. | Item. No. | Item Description | Q'ty | Mode |  |  | Cooling Water |  | Nitrogen |  | Instrument Air |  | REMARK | REMARK
[7 empty] | Flow | Press | Flow | Press | Flow | Press
|  |  |  | C | I | S | Kg/hr | BarABS | Nm3/hr | BarABS | Nm3/hr | BarABS
1 | 44E-40001 | Suction Cooler | 1 | 1 |  |  | Later | 4.5 / 5.5 / 7.0 (8.5)
2 | 44E-40002A/B | Discharge Cooler | 2 | 1 |  | 1 | Later | 4.5 / 5.5 / 7.0 (8.5)
|  | Total Consumption (Kg/hr) |  |  |  |  | 0
|  | Safety Factor |  |  |  |  | 1.2 | 20%
|  | Used Consumption (Kg/hr) |  |  |  |  | 0
3 | - | N2 Line (44Z-20002A/B Conveying) | 1 | 1 |  |  |  |  | 1635 | 4.5 / 5.0 / 5.5 (7.0) |  |  | PN01
4 | 44C-40001A/B | Compressor Seal Purge | 2 | 1 |  | 1 |  |  | Later | 4.5 / 5.0 / 5.5 (7.0) |  |  | PN01
5 | 44V-20001A/B | Blow Tank Purge Line | 2 | 2 |  |  |  |  | 750 | 37 / 39 / 41 (45) |  |  | PHN |  | 사업주 정보제공함 375kg/hr
6 | 44F-20002 | Vent Filter | 1 | 1 |  |  |  |  | 7 | 37 / 39 / 41 (45) |  |  | PHN
7 | 44F-40002A/B | Vent Filter | 2 | 2 |  |  |  |  | 14 | 7.0 / 7.5 / 9.0 (11.5) |  |  | PN03
8 | 44S-40001A/B | Separator | 2 | 2 |  |  |  |  | 126 | 7.0 / 7.5 / 9.0 (11.5) |  |  | PN03
9 | 44F-40001A/B | Silo Vent Filter | 2 | 2 |  |  |  |  | 54 | 4.5 / 5.0 / 5.5 (7.0) |  |  | IN01
10 | 44Z-20002A/B | Conveying Station Seal Purge | 2 |  | 2 |  |  |  | 8.4 | 4.5 / 5.0 / 5.5 (7.0) |  |  | Note. 3, PN01 |  | 12"
11 | 44Z-40001A/B | Conveying Station Seal Purge | 2 | 2 |  |  |  |  | 16.2 | 4.5 / 5.0 / 5.5 (7.0) |  |  | Note. 3, PN01 |  | 20"
12 | 44Z-40002A/B | Rotary Valve Seal Purge | 2 | 2 |  |  |  |  | 16.2 | 4.5 / 5.0 / 5.5 (7.0) |  |  | Note. 3, PN01 |  | 20"
13 | 44Z-40003A/B | Rotary Valve Seal Purge | 2 | 2 |  |  |  |  | 16.2 | 4.5 / 5.0 / 5.5 (7.0) |  |  | Note. 3, PN01 |  | 20"
14 | 44Z-40004A/B | Rotary Valve Seal Purge | 2 | 2 |  |  |  |  | 16.2 | 4.5 / 5.0 / 5.5 (7.0) |  |  | Note. 3, PN01 |  | 20"
15 | 44XV-2007001 | 12" Auto Knife Gate Valve Purge | 1 | 1 |  |  |  |  | 10 | 4.5 / 5.0 / 5.5 (7.0) |  |  | PN01
16 | 44XV-2007002 | 12" Auto Knife Gate Valve Purge | 1 | 1 |  |  |  |  | 10 | 4.5 / 5.0 / 5.5 (7.0) |  |  | PN01
17 | 44XV-2007003 | 12" Auto Knife Gate Valve Purge | 1 | 1 |  |  |  |  | 10 | 4.5 / 5.0 / 5.5 (7.0) |  |  | PN01
18 | 44XV-2007004 | 12" Auto Knife Gate Valve Purge | 1 | 1 |  |  |  |  | 10 | 4.5 / 5.0 / 5.5 (7.0) |  |  | PN01
19 | 44XV-4000001 | 20" Auto Knife Gate Valve Purge | 1 | 1 |  |  |  |  | 10 | 4.5 / 5.0 / 5.5 (7.0) |  |  | PN01
20 | 44XV-4000002 | 20" Auto Knife Gate Valve Purge | 1 | 1 |  |  |  |  | 10 | 4.5 / 5.0 / 5.5 (7.0) |  |  | PN01
21 | 44XV-4003001 | 20" Auto Knife Gate Valve Purge | 1 | 1 |  |  |  |  | 10 | 4.5 / 5.0 / 5.5 (7.0) |  |  | PN01
22 | 44XV-4004001 | 20" Auto Knife Gate Valve Purge | 1 | 1 |  |  |  |  | 10 | 4.5 / 5.0 / 5.5 (7.0) |  |  | PN01
23 | - | 12" Manual Knife Gate Valve Purge | 2 | 2 |  |  |  |  | 20 | 4.5 / 5.0 / 5.5 (7.0) |  |  | PN01
24 | - | 20" Manual Knife Gate Valve Purge | 2 | 2 |  |  |  |  | 20 | 4.5 / 5.0 / 5.5 (7.0) |  |  | PN01
25 | - | 20" Manual Knife Gate Valve Purge | 2 | 2 |  |  |  |  | 20 | 4.5 / 5.0 / 5.5 (7.0) |  |  | PN01
|  | Total Consumption (Nm3/hr) | [6 empty] | 2799.2
|  | Safety Factor | [6 empty] | 1.2 | 20%
|  | Used Consumption (Nm3/hr) | [6 empty] | 3359.04
26 | 44US-40001 | Truck Unloading Station | 1 | 1 | [6 empty] | 2319 | 6.5 / 8.4 / 8.5 (15) | IN01
27 | 44XV-2007014 | 4" Auto Ball Valve | 1 | 1 | [6 empty] | 0.003 | 6.5 / 8.4 / 8.5 (15) | for Stroke
28 | 44XV-2007017 | 4" Auto Ball Valve | 1 | 1 | [6 empty] | 0.003 | 6.5 / 8.4 / 8.5 (15) | for Stroke
29 | 44XV-2007011 | 3" Auto Ball Valve | 1 | 1 | [6 empty] | 0.003 | 6.5 / 8.4 / 8.5 (15) | for Stroke
30 | 44XV-2007008 | 2" Auto Ball Valve | 1 | 1 | [6 empty] | 0.003 | 6.5 / 8.4 / 8.5 (15) | for Stroke
31 | 44XV-2007043 | 2" Auto Ball Valve | 1 | 1 | [6 empty] | 0.003 | 6.5 / 8.4 / 8.5 (15) | for Stroke
32 | 44XV-2007040 | 1" Auto Ball Valve | 1 | 1 | [6 empty] | 0.003 | 6.5 / 8.4 / 8.5 (15) | for Stroke
33 | 44XV-2007041 | 1" Auto Ball Valve | 1 | 1 | [6 empty] | 0.003 | 6.5 / 8.4 / 8.5 (15) | for Stroke
34 | 44XV-2007042 | 8" Auto Ball Valve | 1 | 1 | [6 empty] | 0.003 | 6.5 / 8.4 / 8.5 (15) | for Stroke
35 | 44XV-2007010 | 6" Auto Ball Valve | 1 | 1 | [6 empty] | 0.003 | 6.5 / 8.4 / 8.5 (15) | for Stroke
36 | 44XV-2007012 | 6" Auto Ball Valve | 1 | 1 | [6 empty] | 0.003 | 6.5 / 8.4 / 8.5 (15) | for Stroke
37 | 44XV-2007013 | 6" Auto Ball Valve | 1 | 1 | [6 empty] | 0.003 | 6.5 / 8.4 / 8.5 (15) | for Stroke
38 | 44XV-4003003 | 4" Auto Ball Valve | 1 | 1 | [6 empty] | 0.003 | 6.5 / 8.4 / 8.5 (15) | for Stroke
39 | 44XV-4004004 | 4" Auto Ball Valve | 1 | 1 | [6 empty] | 0.003 | 6.5 / 8.4 / 8.5 (15) | for Stroke
40 | 44XV-2007001 | 12" Auto Knife Gate Valve | 1 | 1 | [6 empty] | 0.01 | 6.5 / 8.4 / 8.5 (15) | for Stroke
41 | 44XV-2007002 | 12" Auto Knife Gate Valve | 1 | 1 | [6 empty] | 0.01 | 6.5 / 8.4 / 8.5 (15) | for Stroke
42 | 44XV-2007003 | 10" Auto Knife Gate Valve | 1 | 1 | [6 empty] | 0.01 | 6.5 / 8.4 / 8.5 (15) | for Stroke
43 | 44XV-2007004 | 10" Auto Knife Gate Valve | 1 | 1 | [6 empty] | 0.01 | 6.5 / 8.4 / 8.5 (15) | for Stroke
44 | 44XV-4000001 | 20" Auto Knife Gate Valve | 1 | 1 | [6 empty] | 0.026 | 6.5 / 8.4 / 8.5 (15) | for Stroke
45 | 44XV-4000002 | 20" Auto Knife Gate Valve | 1 | 1 | [6 empty] | 0.026 | 6.5 / 8.4 / 8.5 (15) | for Stroke
46 | 44XV-4003001 | 20" Auto Knife Gate Valve | 1 | 1 | [6 empty] | 0.026 | 6.5 / 8.4 / 8.5 (15) | for Stroke
47 | 44XV-4004001 | 20" Auto Knife Gate Valve | 1 | 1 | [6 empty] | 0.026 | 6.5 / 8.4 / 8.5 (15) | for Stroke
48 | 44XV-5000005 | 14" Auto Knife Gate Valve | 1 | 1 | [6 empty] | 0.01 | 6.5 / 8.4 / 8.5 (15) | for Stroke
49 | 44XV-2007005 | 3" Auto Butterfly Valve | 1 | 1 | [6 empty] | 0.003 | 6.5 / 8.4 / 8.5 (15) | for Stroke
50 | 44XV-2007019 | 12" Auto Butterfly Valve | 1 | 1 | [6 empty] | 0.003 | 6.5 / 8.4 / 8.5 (15) | for Stroke
51 | 44XV-2007020 | 12" Auto Butterfly Valve | 1 | 1 | [6 empty] | 0.003 | 6.5 / 8.4 / 8.5 (15) | for Stroke
52 | 44XV-4000010 | 10" Auto Butterfly Valve | 1 | 1 | [6 empty] | 0.003 | 6.5 / 8.4 / 8.5 (15) | for Stroke
53 | 44XV-4000011 | 10" Auto Butterfly Valve | 1 | 1 | [6 empty] | 0.003 | 6.5 / 8.4 / 8.5 (15) | for Stroke
54 | 44XV-4000016 | 20" Auto Butterfly Valve | 1 | 1 | [6 empty] | 0.003 | 6.5 / 8.4 / 8.5 (15) | for Stroke
55 | 44XV-4000017 | 20" Auto Butterfly Valve | 1 | 1 | [6 empty] | 0.003 | 6.5 / 8.4 / 8.5 (15) | for Stroke
56 | 44XV-4001001 | 10" Auto Butterfly Valve | 1 | 1 | [6 empty] | 0.003 | 6.5 / 8.4 / 8.5 (15) | for Stroke
57 | 44XV-4002001 | 10" Auto Butterfly Valve | 1 | 1 | [6 empty] | 0.003 | 6.5 / 8.4 / 8.5 (15) | for Stroke
58 | 44XV-4003009 | 3" Auto Butterfly Valve | 1 | 1 | [6 empty] | 0.003 | 6.5 / 8.4 / 8.5 (15) | for Stroke
59 | 44XV-4003004 | 20" Auto Butterfly Valve | 1 | 1 | [6 empty] | 0.003 | 6.5 / 8.4 / 8.5 (15) | for Stroke
60 | 44XV-4004004 | 20" Auto Butterfly Valve | 1 | 1 | [6 empty] | 0.003 | 6.5 / 8.4 / 8.5 (15) | for Stroke
61 | 44XV-5001011 | 14" Auto Butterfly Valve | 1 | 1 | [6 empty] | 0.003 | 6.5 / 8.4 / 8.5 (15) | for Stroke
62 | 44L-40001 | 8" Auto 3-Way Diverter Valve (Ball) | 1 | 1 | [6 empty] | 0.003 | 6.5 / 8.4 / 8.5 (15) | for Stroke
63 | 44L-40002 | 10" Auto 3-Way Diverter Valve (Ball) | 1 | 1 | [6 empty] | 0.003 | 6.5 / 8.4 / 8.5 (15) | for Stroke
64 | 44L-50002 | 14" Auto 3-Way Diverter Valve (Flat) | 1 | 1 | [6 empty] | 0.003 | 6.5 / 8.4 / 8.5 (15) | for Stroke
65 | 44L-50001A | 16" Auto 3-Way Diverter Valve (Flat) | 1 | 1 | [6 empty] | 0.003 | 6.5 / 8.4 / 8.5 (15) | for Stroke
66 | 44L-50001B | 16" Auto 3-Way Diverter Valve (Flat) | 1 | 1 | [6 empty] | 0.003 | 6.5 / 8.4 / 8.5 (15) | for Stroke
67 | 44L-50004 | 14" Auto 3-Way Diverter Valve (Flat) | 1 | 1 | [6 empty] | 0.003 | 6.5 / 8.4 / 8.5 (15) | for Stroke
|  | Total Consumption (Nm3/hr) | [8 empty] | 2319.25
|  | Safety Factor | [8 empty] | 1.2 | 20%
|  | Used Consumption (Nm3/hr) | [8 empty] | 2783.1
Note | 1. Legend ; C : Continuous, I : Intermittent, S : Stand-by
2. Utility Conditions at the Battery Limit per BEDD shall be considered.
3. Nill : Normal Operation (10Nm3/hr : Seal Broken Operation)
Note on H4: Please select required utilities such as Cooling Water, Plant Water, Polished Water, Drinking Water, Nitorgen, Instrument Air, Plant Air, HP Seam, MP Steam, LP Steam, Fuel Gas, Fuel Oil
Note on J4: Please select required utilities such as Cooling Water, Plant Water, Polished Water, Drinking Water, Nitorgen, Instrument Air, Plant Air, HP Seam, MP Steam, LP Steam, Fuel Gas, Fuel Oil
Note on L4: Please select required utilities such as Cooling Water, Plant Water, Polished Water, Drinking Water, Nitorgen, Instrument Air, Plant Air, HP Seam, MP Steam, LP Steam, Fuel Gas, Fuel Oil

## SAMPLE
UTILITY CONSUMPTION LIST
[7 empty] | 1 | 1
No. | Item. No. | Item Description | Q'ty | Mode |  |  | HP Steam |  | Cooling Water |  | Nitrogen |  | Instrument Air |  | REMARK | REMARK
[7 empty] | Flow | Press | Flow | Press | Flow | Press | Flow | Press
[7 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
[7 empty] | NM3/Hr | Kgf/cm2(g) | NM3/Hr | Kgf/cm2(g) | NM3/Hr | Kgf/cm2(g) | NM3/Hr | Kgf/cm2(g)
[7 empty] | M3/Hr | Mpa(g) | M3/Hr | Mpa(g) | M3/Hr | Mpa(g) | M3/Hr | Mpa(g)
[7 empty] | L/Hr | Bar(g) | L/Hr | Bar(g) | L/Hr | Bar(g) | L/Hr | Bar(g)
[7 empty] | L/Min | mbar(g) | L/Min | mbar(g) | L/Min | mbar(g) | L/Min | mbar(g)
[7 empty] | Kg/Hr | mmWTR | Kg/Hr | mmWTR | Kg/Hr | mmWTR | Kg/Hr | mmWTR
[7 empty] | Ton/Hr | mmHg | Ton/Hr | mmHg | Ton/Hr | mmHg | Ton/Hr | mmHg
|  |  |  | C | I | S | Ton/Hr | Mpa(g) | M3/Hr | Mpa(g) | NM3/Hr | Mpa(g) | NM3/Hr | Mpa(g)
1 | 8121-TR-101 | Steam Turbine for compressor | 1 | 1 |  |  | 82022 | 3.73
2 | 8121-E-111 A/B | Oil cooler | 2 | 1 |  | 1 |  |  | 45.7 | 0.5
3 | - | Seal gas for Dry gas sealing compressor | 1 | [7 empty] | 33 | 0.3
4 | - | Seal gas for sealing gas turbine | 1 | [7 empty] | 122 | 0.3
5 | 8121-K-111 A/B | Seal gas panel - Booster | 2 | 1 |  | 1 | [6 empty] | 45.5 | 0.4
6 | 8121-J-122 | Gland steam ejector | 1 |  |  |  | 30 | 5.55
7 | 8121-E-122 | Gland steam condenser | 1 | [5 empty] | 60 | 0.5
Note | 1. Legend ; C : Continuous, I : Intermittent, S : Stand-by
2. Utility Conditions at the Battery Limit per BEDD shall be considered.
3. Measurement Unit shall be followed according to Project Specification.
※ No part of this document may be circulated, quoted, or reproduced without prior written approval from Daelim. ※ 이 정보(문서)는 대림산업㈜의 자산으로서, 허가 없는 사회반출을 금지합니다.
REFERENCE ONLY
Note on H5: Please select required utilities such as Cooling Water, Plant Water, Polished Water, Drinking Water, Nitorgen, Instrument Air, Plant Air, HP Seam, MP Steam, LP Steam, Fuel Gas, Fuel Oil
Note on J5: Please select required utilities such as Cooling Water, Plant Water, Polished Water, Drinking Water, Nitorgen, Instrument Air, Plant Air, HP Seam, MP Steam, LP Steam, Fuel Gas, Fuel Oil
Note on L5: Please select required utilities such as Cooling Water, Plant Water, Polished Water, Drinking Water, Nitorgen, Instrument Air, Plant Air, HP Seam, MP Steam, LP Steam, Fuel Gas, Fuel Oil
Note on N5: Please select required utilities such as Cooling Water, Plant Water, Polished Water, Drinking Water, Nitorgen, Instrument Air, Plant Air, HP Seam, MP Steam, LP Steam, Fuel Gas, Fuel Oil
Note on H14: Please select the measurement unit per project specification.
Note on I14: Please select the measurement unit per project specification.
Note on J14: Please select the measurement unit per project specification.
Note on K14: Please select the measurement unit per project specification.
Note on L14: Please select the measurement unit per project specification.
Note on M14: Please select the measurement unit per project specification.
Note on N14: Please select the measurement unit per project specification.
Note on O14: Please select the measurement unit per project specification.

## 참고
UTILITY CONSUMPTION LIST
No. | Item. No. | Item Description | Q'ty | Mode |  |  | Cooling Water |  | Nitrogen |  | Instrument Air |  | REMARK | REMARK | old
[7 empty] | Flow | Press | Flow | Press | Flow | Press |  |  | Compressor Cooling Water |  |  | Cooler Cooling Water
|  |  |  | C | I | S | gpm | psig | lb/hr | psig | scfh | psig |  |  | Nm/h3 | kg/hr | lb/hr | lb/hr | kg/hr | Nm/h3 | gpm
1 | 20-E-6005A | Fluff Transfer Compressor | 1 | C: 1; gpm: 178; psig: 80 | Note.6 |  | 26->35 | 35000 | 77161 | 102343 | 46422.01 | 46.422 | 204.38
2 | 20-E-6005B | Fluff Transfer Compressor | 1 | C: 1; gpm: 178; psig: 80 | Note.6 |  | gpm |  |  | ->121393 | 55062.94 | 55.062 | 242.4
3 | 20-E-6005C | Fluff Transfer Compressor | 1 | S: 1; gpm: 178; psig: 80 | Note.6 |  | -> 154
4 | 20-E-6004 | Fluff Transfer Compressor Suction Cooler | 1 | C: 1; gpm: 242.4; psig: 80 |  |  | Latest
|  | Total Consumption (gpm) |  | gpm: 776.4 |  |  | 178.59 gpm | (=40.5 Nm3/hr)
|  | Safety Factor |  | gpm: 1.2; psig: 20% |  |  |  |  | N2 밀도
|  | Used Consumption (gpm) |  | gpm: 931.68 |  |  | gpm | Nm3/h | 1.251 | kg/h | lb/hr
5 | 20-Y-5001 | Purge Column Rotary Valve | 1 | C: 1; lb/hr: Nill; psig: 45 / 50 / 55 | LP N2, Note. 4 |  | 620.1 | 140.84 | 176.1908 | 176.2 | 388.45
6 | 20-Y-6003 | Fluff Silo Rotary Valve | 1 | C: 1; lb/hr: Nill; psig: 45 / 50 / 55 | LP N2, Note. 5 |  | 691.2 | 156.98 | 196.382 | 196.39 | 432.97
7 | 20-F-6002 | Extruder Feeder Tank Vent Filter | 1 | C: 1; lb/hr: 388.45; psig: 170 | MP N2 |  | 87.5 | 19.87 | 24.8574 | 24.86 | 54.8
8 | 20-F-6003 | Fluff Silo Vent Filter | 1 | C: 1; lb/hr: 432.97; psig: 170 | MP N2 |  | 351.5 | 79.83 | 99.8673 | 99.87 | 220.18
9 | 20-XV-600116 | 10"-Diverter Valve | 1 | C: 1; lb/hr: Nill; psig: 45 / 50 / 55 | LP N2, Note. 7 |  | 117.4 | 26.66 | 33.3517 | 33.36 | 73.55
10 | 20-XV-600121 | 16"-Auto Knife Gate Valve | 1 | C: 1; lb/hr: Max. 18.43; psig: 45 / 50 / 55 | LP N2
11 | 20-XV-500206 | 24"-Auto Knife Gate Valve | 1 | C: 1; lb/hr: Max. 18.43; psig: 45 / 50 / 55 | LP N2
12 | 20-SP-6085, 6090 | 12"-Manual Knife Gate Valve | 2 | C: 2; lb/hr: Max. 36.86; psig: 45 / 50 / 55 | LP N2 |  | Slide -> Knife 로 수정
13 | 20-SP-6086 | 20"-Manual Knife Gate Valve | 1 | C: 1; lb/hr: Max. 18.43; psig: 45 / 50 / 55 | LP N2 |  | Manual Knife Gate Auto랑 동일하게
14 | 20-SP-5077 | 30"-Manual Knife Gate Valve | 1 | C: 1; lb/hr: Max. 18.43; psig: 45 / 50 / 55 | LP N2 |  | Diverter는 RV랑 동일하게
|  | Total Consumption (lb/hr) |  | lb/hr: 895.14
|  | Safety Factor |  | lb/hr: 1.2; psig: 20%
|  | Used Consumption (lb/hr) |  | lb/hr: 1074.168
15 | 20-E-6005A | Fluff Transfer Compressor After Breather | 1 | C: 1; scfh: 247.04; psig: 80 / 105 / 130 | I.A for Breather
16 | 20-E-6005B | Fluff Transfer Compressor After Breather | 1 | C: 1; scfh: 247.04; psig: 80 / 105 / 130 | I.A for Breather
17 | 20-E-6005C | Fluff Transfer Compressor After Breather | 1 | S: 1; scfh: 247.04; psig: 80 / 105 / 130 | I.A for Breather
18 | 20-XV-600116 | 10"-Diverter Valve | 1 | C: 1; scfh: 3.6; psig: 80 / 105 / 130 | for Stroke
19 | 20-XV-600121 | 16"-Auto Knife Gate Valve | 1 | C: 1; scfh: 9.54; psig: 80 / 105 / 130 | for Stroke
20 | 20-XV-500206 | 24"-Auto Knife Gate Valve | 1 | C: 1; scfh: 6.41; psig: 80 / 105 / 130 | for Stroke
21 | 20-XV-600115 | 20"-Auto Butterfly Valve | 1 | C: 1; scfh: 3.6; psig: 80 / 105 / 130 | for Stroke
22 | - | PLC Panel Purge IA | 1 | C: 1; scfh: 0.353
|  | Total Consumption (scfh) |  | scfh: 764.623
|  | Safety Factor |  | scfh: 1.2; psig: 20%
|  | Used Consumption (scfh) |  | scfh: 917.5476
Note | 1. Legend ; C : Continuous, I : Intermittent, S : Stand-by |  |  | S: 4. Nill : Normal Operation; psig: 6. Cooling Water for; psig: 7. Nill : Normal Operation
| 2. Utility Conditions at the Battery Limit per BEDD shall be considered. |  |  | S: 18.43 lb/hr : Seal Broken Operation; psig: 1) After cooler; psig: If Required, Use within a range of xx to xx lb/hr
| 3. Measurement Unit shall be followed according to Project Specification. |  |  | S: 5. Nill : Normal Operation; psig: 2) Compressor casing
[6 empty] | 18.43 lb/hr : Seal Broken Operation |  |  |  | 3) Lube oil cooler
CONFIDENTIAL AND PROPRIETARY INFORMATION: This information is proprietary and shall not be used, copied, disseminated or disclosed for any purposes other than those permitted under written agreement with Golden Triangle Polymers Company LLC EXPORT OF TECHNOLOGY: This technology is subject to U.S. Export Control Laws; Diversion Contrary to U.S. Law prohibited.
1 | 21-E-6005A | Fluff Transfer Compressor After Cooler | 1 | C: 1; gpm: 57320; psig: 80; scfh: 30.8; psig: 80 / 105 / 130 | IA for Breather
2 | 21-E-6005B | Fluff Transfer Compressor After Cooler | 1 | C: 1; gpm: 57320; psig: 80; scfh: 30.8; psig: 80 / 105 / 130 | IA for Breather
3 | 21-E-6005C | Fluff Transfer Compressor After Cooler | 1 | S: 1; gpm: 57320; psig: 80; scfh: 30.8; psig: 80 / 105 / 130 | IA for Breather
4 | 21-E-6004A | Fluff Transfer Compressor Suction Cooler | 1 | C: 1; gpm: 106000.5; psig: 80
5 | 21-E-6004B | Fluff Transfer Compressor Suction Cooler | 1 | S: 1; gpm: 106000.5; psig: 80
|  | Total Consumption (lb/hr) |  | gpm: 383961
|  | Safety Factor |  | gpm: 1.2; psig: 20%
|  | Used Consumption (lb/hr) |  | gpm: 460753.2
6 | 21-Y-5001 | Purge Column Rotary Valve | 1 | C: 1; lb/hr: Nill; psig: 45 / 50 / 55 | LP N2, Note. 4
7 | 21-Y-6003 | Fluff Silo Rotary Valve | 1 | C: 1; lb/hr: Nill; psig: 45 / 50 / 55 | LP N2, Note. 5
8 | 21-F-6002 | Extruder Feeder Tank Vent Filter | 1 | C: 1; lb/hr: 620.1; psig: 45 / 50 / 55 | LP N2
9 | 21-F-6003 | Fluff Silo Vent Filter | 1 | C: 1; lb/hr: 691.2; psig: 45 / 50 / 55 | LP N2
10 | 21-HS-600121 | 16"-Auto Slide Valve | 1 | C: 1; lb/hr: 87.5; psig: 45 / 50 / 55 | LP N2
11 | 21-XV-500206 | 24"-Auto Slide Valve | 1 | C: 1; lb/hr: 87.5; psig: 45 / 50 / 55 | LP N2
|  | Total Consumption (gpm) |  | lb/hr: 1486.3
|  | Safety Factor |  | lb/hr: 1.2; psig: 20%
|  | Used Consumption (gpm) |  | lb/hr: 1783.56
12 | 21-XV-600116 | 12"-Diverter Valve | 1 | C: 1; scfh: 0.45; psig: 80 / 105 / 130 | Per Stroke
13 | 21-HS-600121 | 16"-Auto Slide Valve | 1 | C: 1; scfh: 1.19; psig: 80 / 105 / 130 | Per Stroke
14 | 21-XV-500206 | 24"-Auto Slide Valve | 1 | C: 1; scfh: 0.8; psig: 80 / 105 / 130 | Per Stroke
15 | 21-XV-600115 | 20"-Auto Butterfly Valve | 1 | C: 1; scfh: 0.45; psig: 80 / 105 / 130 | Per Stroke
|  | Total Consumption (gpm) |  | scfh: 95.29
|  | Safety Factor |  | scfh: 1.2; psig: 20%
|  | Used Consumption (gpm) |  | scfh: 114.348
Note | 1. Legend ; C : Continuous, I : Intermittent, S : Stand-by |  |  | S: 4. Nill : Normal Operation
| 2. Utility Conditions at the Battery Limit per BEDD shall be considered. |  |  | S: 351.5 gpm : Seal Broken Operation
| 3. Measurement Unit shall be followed according to Project Specification. |  |  | S: 5. Nill : Normal Operation
117.4 gpm : Seal Broken Operation
CONFIDENTIAL AND PROPRIETARY INFORMATION: This information is proprietary and shall not be used, copied, disseminated or disclosed for any purposes other than those permitted under written agreement with Golden Triangle Polymers Company LLC EXPORT OF TECHNOLOGY: This technology is subject to U.S. Export Control Laws; Diversion Contrary to U.S. Law prohibited.
Note on H4: Please select required utilities such as Cooling Water, Plant Water, Polished Water, Drinking Water, Nitorgen, Instrument Air, Plant Air, HP Seam, MP Steam, LP Steam, Fuel Gas, Fuel Oil
Note on J4: Please select required utilities such as Cooling Water, Plant Water, Polished Water, Drinking Water, Nitorgen, Instrument Air, Plant Air, HP Seam, MP Steam, LP Steam, Fuel Gas, Fuel Oil
Note on L4: Please select required utilities such as Cooling Water, Plant Water, Polished Water, Drinking Water, Nitorgen, Instrument Air, Plant Air, HP Seam, MP Steam, LP Steam, Fuel Gas, Fuel Oil