## Powder_LIST
[9 empty] | PROJECT NO. : |  | 3944 | INSTRUMENT INDEX | [41 empty] | 향후 필요시 추가 고려 ---> only for IMPORT into AVEVA ( HOLD )
[9 empty] | MR NO. : |  | 0171
|  |  | 아래 분리 TAG는 실제 입력 대상이고, 공식 출력물에서는 나타나지 않음 | [5 empty] | DOC TITLE : |  | Instrument Index | [30 empty] | IO LIST용 추가 COLUMN (DB에 해당 FIELD 생성) | [11 empty] | Process data |  |  | Operating Condition | [11 empty] | Design Data
[9 empty] | DOC NO. : |  | 3944-VD-0171-DYP-RE-400-INX-0076
[9 empty] | REV : |  | 01
|  | delete | [7 empty] | delete |  |  |  |  | delete |  | delete | [8 empty] | delete | [8 empty] | DELETE |  |  | delete | [18 empty] | Flow |  |  |  | Temperature |  |  |  | Pressure |  |  |  | Design Pressure | Design Temp. | Diff. Pressure | Shutoff Pressure | Back Pressure (Total)
REV | PLANT | UNIT | Tag | No. | Suffix | TAG NO. | P&ID No. | FLUID | FLUID STATUS | SERVICE (수정전) | SERVICE | INST.TYPE | SCOPE | LOC. (From/To) | SYSTEM | IO TYPE | SYSTEM LOC. | SIGNAL TYPE | IS/NIS | EXT.POWER | CALIB. RANGE MIN | CALIB. RANGE MAX | CALIB. RANGE UNIT | MANUFACTURER | MODEL | SCALE RANGE UNIT | INST.SIZE (INLET) | INST.RATING (INLET) | INST.SIZE (OUTLET) | INST.RATING (OUTLET) | MATL.BODY | MATL.ELEM | VALVE FAIL | LINE SIZE | LINE SPEC | LINE NO. | EQUIPT NO. | PKG NO. | ACC. | PO NO. | REMARK | EXTER. POWER | IS/NIS | CONTACT STATUS | LOGIC No. | CONTROLLER ACTION | DCS RANGE MIN | DCS RANGE MAX | DCS RANGE UNIT | ALARM SP_LL | ALARM SP_L | ALARM SP_H | ALARM SP_HH | Specific Gravity | Viscosity | Molecular Weight | Min. | Nor. | Max | Unit | Min. | Nor. | Max | Unit | Min. | Nor. | Max | Unit
P&ID NO. : 20070
1 | 44 | 200 | XV | 2007001 |  | 44XV-2007001 | 20070 | PE | S | XV-2007001 KNIFE GATE VALVE | 44TK-20001A INLET KNIFE GATE VALVE | KNIFE GATE ON/OFF VALVE | DYPNF | FIELD | - | - | - | - | - | - | - | - | - | LATER | LATER | - | 12" | 150# LUG | 12" | 150# LUG | A351 CF8M | A240 316 (Hcr Coating) | FL | 12" | AKRB7 | 12"-PE01-2007022-AKRB7-P30 | - | 44W-40001 | -
1 | 44 | 200 | XVYA | 2007001 |  | 44XVYA-2007001 | 20070 | - | - | XV-2007001 KNIFE GATE VALVE OPEN COMMAND | 44TK-20001A INLET KNIFE GATE OPEN SOLENOID VALVE | SOLENOID VALVE |  | DCS/FIELD | DCS | DO | DCS | 24VDC | IS | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 44W-40001 | - | -
1 | 44 | 200 | XVYB | 2007001 |  | 44XVYB-2007001 | 20070 | - | - | XV-2007001 KNIFE GATE VALVE CLOSE COMMAND | 44TK-20001A INLET KNIFE GATE CLOSE SOLENOID VALVE | SOLENOID VALVE |  | DCS/FIELD | DCS | DO | DCS | 24VDC | IS | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 44W-40001 | - | -
1 | 44 | 200 | ZSH | 2007001 |  | 44ZSH-2007001 | 20070 | - | - | XV-2007001 OPEN LIMIT SWITCH | 44TK-20001A INLET KNIFE GATE OPEN LIMIT SWITCH | LIMIT SWITCH |  | FIELD/DCS | DCS | DI | DCS | NAMUR | IS | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 44W-40001 | - | -
1 | 44 | 200 | ZSL | 2007001 |  | 44ZSL-2007001 | 20070 | - | - | XV-2007001 CLOSE LIMIT SWITCH | 44TK-20001A INLET KNIFE GATE CLOSE LIMIT SWITCH | LIMIT SWITCH |  | FIELD/DCS | DCS | DI | DCS | NAMUR | IS | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 44W-40001 | - | -
ES
ES
ES
ES
ES
ES
ES
ES
ES
ES
ES

## Sheet1
44FT-2007060 | POWDER CONVEYING N2 SUPPLY FLOW | 44FT-2007060
44PT-2007062 | POWDER CONVEYING N2 SUPPLY PRESSURE | 44PT-2007062
44PT-2007019 | 44Z-20002A CONVEYING STATION PURGING PRESSURE | 44PT-2007019
44PT-2007020 | 44Z-20002B CONVEYING STATION PURGING PRESSURE | 44PT-2007020
44PDT-2007003 | 44F-20002 VENT FILTER DIFF. PRESSURE | 44PDT-2007003
44LSH-2007003A | 44V-20001A BLOW TANK LEVEL HIGH SWITCH | 44LSH-2007003A
44LSL-2007002A | 44V-20001A BLOW TANK LEVEL LOW SWITCH | 44LSL-2007002A
44LSH-2007003B | 44V-20001B BLOW TANK LEVEL HIGH SWITCH | 44LSH-2007003B
44LSL-2007002B | 44V-20001B BLOW TANK LEVEL LOW SWITCH | 44LSL-2007002B
44PDT-4000003 | 44F-40002A VENT FILTER DIFF. PRESSURE | 44PDT-4000003
44PT-4000005 | 44V-40001A FEED HOPPER PRESSURE | 44PT-4000005
44PDT-4000013 | 44F-40002B VENT FILTER DIFF. PRESSURE | 44PDT-4000013
44PT-4000015 | 44V-40001B FEED HOPPER PRESSURE | 44PT-4000015
44PT-4000004 | 44Z-40001A CONVEYING STATION PURGING PRESSURE | 44PT-4000004
44PT-4000014 | 44Z-40001B CONVEYING STATION PURGING PRESSURE | 44PT-4000014
44PT-4000001 | 44V-40001A OUTLET CONVEYING LINE PRESSURE | 44PT-4000001
44PT-4000011 | 44V-40001B OUTLET CONVEYING LINE PRESSURE | 44PT-4000011
44PT-4001001 | 44C-40001A/B POWDER CONVEYING SYSTEM N2 SUPPLY PRESSURE | 44PT-4001001
44TT-4001052 | 44C-40001A/B CONVEYING GAS COMPRESSOR SUCTION TEMPERATURE | 44TT-4001052
44PDT-4001002 | 44C-40001A GAURD FILTER(44F-40003A) DIFF. PRESSURE | 44PDT-4001002
44PT-4001003 | 44C-40001A CONVEYING GAS COMPRESSOR SUCTION PRESSURE | 44PT-4001003
44TT-4001001 | 44C-40001A CONVEYING GAS COMPRESSOR TEMPERATURE | 44TT-4001001
44PDT-4001010 | 44C-40001A CONVEYING GAS COMPRESSOR DIFF. PRESSURE | 44PDT-4001010
44PT-4001011 | 44C-40001A CONVEYING GAS COMPRESSOR OUTLET PRESSURE | 44PT-4001011
44TT-4001002 | 44C-40001A CONVEYING GAS COMPRESSOR OUTLET TEMPERATURE-1 (1 of 2) | 44TT-4001002
44TT-4001003 | 44C-40001A CONVEYING GAS COMPRESSOR OUTLET TEMPERATURE-2 (1 of 2) | 44TT-4001003
44TS-4001057 | 44C-40001A CONVEYING GAS COMPRESSOR OUTLET TEMPERATURE HIGH SWITCH | 44TS-4001057
44TT-4001005 | 44C-40001A DISCHARGE COOLER(44E-40002A) OUTLET TEMPERATURE | 44TT-4001005
44PS-4001054 | 44C-40001A CONVEYING GAS COMPRESSOR INLET PRESSURE SWITCH | 44PS-4001054
44TS-4001056 | 44C-40001A CONVEYING GAS COMPRESSOR INLET TEMPERATURE SWITCH | 44TS-4001056
44PDT-4002002 | 44C-40001B GAURD FILTER(44F-40003B) DIFF. PRESSURE | 44PDT-4002002
44PT-4002003 | 44C-40001B CONVEYING GAS COMPRESSOR SUCTION PRESSURE | 44PT-4002003
44TT-4002001 | 44C-40001B CONVEYING GAS COMPRESSOR TEMPERATURE | 44TT-4002001
44PDT-4002010 | 44C-40001B CONVEYING GAS COMPRESSOR DIFF. PRESSURE | 44PDT-4002010
44PT-4002011 | 44C-40001B CONVEYING GAS COMPRESSOR OUTLET PRESSURE | 44PT-4002011
44TT-4002002 | 44C-40001B CONVEYING GAS COMPRESSOR OUTLET TEMPERATURE-1 (1 of 2) | 44TT-4002002
44TT-4002003 | 44C-40001B CONVEYING GAS COMPRESSOR OUTLET TEMPERATURE-2 (1 of 2) | 44TT-4002003
44TS-4002057 | 44C-40001B CONVEYING GAS COMPRESSOR OUTLET TEMPERATURE HIGH SWITCH | 44TS-4002057
44TT-4002005 | 44C-40001B DISCHARGE COOLER(44E-40002B) OUTLET TEMPERATURE | 44TT-4002005
44PS-4002054 | 44C-40001B CONVEYING GAS COMPRESSOR INLET PRESSURE SWITCH | 44PS-4002054
44TS-4002056 | 44C-40001B CONVEYING GAS COMPRESSOR INLET TEMPERATURE SWITCH | 44TS-4002056
44PDT-4003003 | 44S-40001A SEPARATOR DIFF. PRESSURE | 44PDT-4003003
44LSH-4003002 | 44S-40001A SEPARATOR LEVEL HIGH SWITCH | 44LSH-4003002
44PT-4003004 | 44Z-40002A ROTARY VALVE N2 PURGING PRESSURE | 44PT-4003004
44PT-4003005 | 44Z-40003A ROTARY VALVE N2 PURGING PRESSURE | 44PT-4003005
44PDT-4003001 | 44F-40001A SILO VENT FILTER DIFF. PRESSURE | 44PDT-4003001
44PT-4003002 | 44Z-40004A ROTARY VALVE N2 PURGING PRESSURE | 44PT-4003002
44PDT-4004003 | 44S-40001B SEPARATOR DIFF. PRESSURE | 44PDT-4004003
44LSH-4004002 | 44S-40001B SEPARATOR LEVEL SWITCH HIGH | 44LSH-4004002
44PT-4004004 | 44Z-40002B ROTARY VALVE N2 PURGING PRESSURE | 44PT-4004004
44PT-4004005 | 44Z-40003B ROTARY VALVE N2 PURGING PRESSURE | 44PT-4004005
44PDT-4004001 | 44F-40001B SILO VENT FILTER DIFF. PRESSURE | 44PDT-4004001
44PT-4004002 | 44Z-40004B ROTARY VALVE N2 PURGING PRESSURE | 44PT-4004002
44LSH-5001002 | 44WS-50001 POWER LOADING DEVICE LEVEL HIGH SWITCH | 44LSH-5001002
44XVYA-2007005 | POWDER CONVEYING N2 SUPPLY VALVE OPEN COMMAND | 44XVYA-2007005
44ZLSH-2007005 | POWDER CONVEYING N2 SUPPLY VALVE OPEN LIMIT SWITCH | 44ZLSH-2007005
44ZLSL-2007005 | POWDER CONVEYING N2 SUPPLY VALVE CLOSE LIMIT SWITCH | 44ZLSL-2007005
44FV-2007060 | POWDER CONVEYING N2 SUPPLY FLOW CONTROL VALVE DEMAND | 44FV-2007060
44FZLH-2007060 | POWDER CONVEYING N2 SUPPLY FLOW CONTROL VALVE OPEN LIMIT SWITCH | 44FZLH-2007060
44FZLL-2007060 | POWDER CONVEYING N2 SUPPLY FLOW CONTROL VALVE CLOSE LIMIT SWITCH | 44FZLL-2007060
44XVYA-2007001 | 44TK-20001A INLET KNIFE GATE OPEN COMMAND | 44XVYA-2007001
44XVYB-2007001 | 44TK-20001A INLET KNIFE GATE CLOSE COMMAND | 44XVYB-2007001
44ZLSH-2007001 | 44TK-20001A INLET KNIFE GATE OPEN LIMIT SWITCH | 44ZLSH-2007001
44ZLSL-2007001 | 44TK-20001A INLET KNIFE GATE CLOSE LIMIT SWITCH | 44ZLSL-2007001
44XVYA-2007003 | 44TK-20001A OUTLET KNIFE GATE OPEN COMMAND | 44XVYA-2007003
44ZLSH-2007003 | 44TK-20001A OUTLET KNIFE GATE OPEN LIMIT SWITCH | 44ZLSH-2007003
44ZLSL-2007003 | 44TK-20001A OUTLET KNIFE GATE CLOSE LIMIT SWITCH | 44ZLSL-2007003
44XVYA-2007019 | 44Z-20002A OUTLET VALVE OPEN COMMAND | 44XVYA-2007019
44XVYB-2007019 | 44Z-20002A OUTLET VALVE CLOSE COMMAND | 44XVYB-2007019
44ZLSH-2007019 | 44Z-20002A OUTLET VALVE OPEN LIMIT SWITCH | 44ZLSH-2007019
44ZLSL-2007019 | 44Z-20002A OUTLET VALVE CLOSE LIMIT SWITCH | 44ZLSL-2007019
44XVY-2007031 | 44Z-20002A PURGING SOL VALVE CLOSE COMMAND | 44XVY-2007031
44XVYA-2007002 | 44TK-20001B INLET KNIFE GATE OPEN COMMAND | 44XVYA-2007002
44XVYB-2007002 | 44TK-20001B INLET KNIFE GATE CLOSE COMMAND | 44XVYB-2007002
44ZLSH-2007002 | 44TK-20001B INLET KNIFE GATE OPEN LIMIT SWITCH | 44ZLSH-2007002
44ZLSL-2007002 | 44TK-20001B INLET KNIFE GATE CLOSE LIMIT SWITCH | 44ZLSL-2007002
44XVYA-2007004 | 44TK-20001B OUTLET KNIFE GATE OPEN COMMAND | 44XVYA-2007004
44ZLSH-2007004 | 44TK-20001B OUTLET KNIFE GATE OPEN LIMIT SWITCH | 44ZLSH-2007004
44ZLSL-2007004 | 44TK-20001B OUTLET KNIFE GATE CLOSE LIMIT SWITCH | 44ZLSL-2007004
44XVYA-2007020 | 44Z-20002B OUTLET VALVE OPEN COMMAND | 44XVYA-2007020
44XVYB-2007020 | 44Z-20002B OUTLET VALVE CLOSE COMMAND | 44XVYB-2007020
44ZLSH-2007020 | 44Z-20002B OUTLET VALVE OPEN LIMIT SWITCH | 44ZLSH-2007020
44ZLSL-2007020 | 44Z-20002B OUTLET VALVE CLOSE LIMIT SWITCH | 44ZLSL-2007020
44XVY-2007032 | 44Z-20002B PURGING SOL VALVE CLOSE COMMAND | 44XVY-2007032
44HS-2007020 | 44F-20002 VENT FILTER TIMER BOX ON COMMAND | 44HS-2007020
44XVYA-2007008 | 44V-20001A BLOW TANK N2 SUPPLY VALVE OPEN COMMAND | 44XVYA-2007008
44ZLSH-2007008 | 44V-20001A BLOW TANK N2 SUPPLY VALVE OPEN LIMIT SWITCH | 44ZLSH-2007008
44ZLSL-2007008 | 44V-20001A BLOW TANK N2 SUPPLY VALVE CLOSE LIMIT SWITCH | 44ZLSL-2007008
44XVYA-2007041 | 44V-20001A BLOW TANK PURGE VALVE OPEN COMMAND | 44XVYA-2007041
44ZLSH-2007041 | 44V-20001A BLOW TANK PURGE VALVE OPEN LIMIT SWITCH | 44ZLSH-2007041
44ZLSL-2007041 | 44V-20001A BLOW TANK PURGE VALVE CLOSE LIMIT SWITCH | 44ZLSL-2007041
44XVYA-2007043 | 44V-20001B BLOW TANK N2 SUPPLY VALVE OPEN COMMAND | 44XVYA-2007043
44ZLSH-2007043 | 44V-20001B BLOW TANK N2 SUPPLY VALVE OPEN LIMIT SWITCH | 44ZLSH-2007043
44ZLSL-2007043 | 44V-20001B BLOW TANK N2 SUPPLY VALVE CLOSE LIMIT SWITCH | 44ZLSL-2007043
44XVYA-2007040 | 44V-20001B BLOW TANK PURGE VALVE OPEN COMMAND | 44XVYA-2007040
44ZLSH-2007040 | 44V-20001B BLOW TANK PURGE VALVE OPEN LIMIT SWITCH | 44ZLSH-2007040
44ZLSL-2007040 | 44V-20001B BLOW TANK PURGE VALVE CLOSE LIMIT SWITCH | 44ZLSL-2007040
44XVYA-4000001 | 44V-40001A FEED HOPPER INLET KNIFE GATE OPEN COMMAND | 44XVYA-4000001
44XVYB-4000001 | 44V-40001A FEED HOPPER INLET KNIFE GATE CLOSE COMMAND | 44XVYB-4000001
44ZLSH-4000001 | 44V-40001A FEED HOPPER INLET KNIFE GATE OPEN LIMIT SWITCH | 44ZLSH-4000001
44ZLSL-4000001 | 44V-40001A FEED HOPPER INLET KNIFE GATE CLOSE LIMIT SWITCH | 44ZLSL-4000001
44XVYA-4000016 | 44Z-40001A OUTLET VALVE OPEN COMMAND | 44XVYA-4000016
44XVYB-4000016 | 44Z-40001A OUTLET VALVE CLOSE COMMAND | 44XVYB-4000016
44ZLSH-4000016 | 44Z-40001A OUTLET VALVE OPEN LIMIT SWITCH | 44ZLSH-4000016
44ZLSL-4000016 | 44Z-40001A OUTLET VALVE CLOSE LIMIT SWITCH | 44ZLSL-4000016
44ZLSH-4000014 | 44V-40001A FEED HOPPER OUTLET MANUAL VALVE OPEN LIMIT SWITCH | 44ZLSH-4000014
44PDV-4000002 | 44V-40001A FEED HOPPER PRESSURE CONTROL VALVE DEMAND | 44PDV-4000002
44PZLH-4000002 | 44V-40001A FEED HOPPER PRESSURE CONTROL VALVE OPEN LIMIT SWITCH | 44PZLH-4000002
44PZLL-4000002 | 44V-40001A FEED HOPPER PRESSURE CONTROL VALVE CLOSE LIMIT SWITCH | 44PZLL-4000002
44XVY-4000008 | 44Z-40001A PURGING SOL VALVE CLOSE COMMAND | 44XVY-4000008
44HVY-4000030A | 44F-40002A VENT FILTER AIR PULSING SOL VALVE OPEN COMMAND | 44HVY-4000030A
44XVYA-4000002 | 44V-40001B FEED HOPPER INLET KNIFE GATE OPEN COMMAND | 44XVYA-4000002
44XVYB-4000002 | 44V-40001B FEED HOPPER INLET KNIFE GATE CLOSE COMMAND | 44XVYB-4000002
44ZLSH-4000002 | 44V-40001B FEED HOPPER INLET KNIFE GATE OPEN LIMIT SWITCH | 44ZLSH-4000002
44ZLSL-4000002 | 44V-40001B FEED HOPPER INLET KNIFE GATE CLOSE LIMIT SWITCH | 44ZLSL-4000002
44XVYA-4000017 | 44Z-40001B OUTLET VALVE OPEN COMMAND | 44XVYA-4000017
44XVYB-4000017 | 44Z-40001B OUTLET VALVE CLOSE COMMAND | 44XVYB-4000017
44ZLSH-4000017 | 44Z-40001B OUTLET VALVE OPEN LIMIT SWITCH | 44ZLSH-4000017
44ZLSL-4000017 | 44Z-40001B OUTLET VALVE CLOSE LIMIT SWITCH | 44ZLSL-4000017
44ZLSH-4000015 | 44V-40001B FEED HOPPER OUTLET MANUAL VALVE OPEN LIMIT SWITCH | 44ZLSH-4000015
44PDV-4000012 | 44V-40001B FEED HOPPER PRESSURE CONTROL VALVE DEMAND | 44PDV-4000012
44PZLH-4000012 | 44V-40001B FEED HOPPER PRESSURE CONTROL VALVE OPEN LIMIT SWITCH | 44PZLH-4000012
44PZLL-4000012 | 44V-40001B FEED HOPPER PRESSURE CONTROL VALVE CLOSE LIMIT SWITCH | 44PZLL-4000012
44XVY-4000009 | 44Z-40001B PURGING SOL VALVE CLOSE COMMAND | 44XVY-4000009
44HVY-4000040A | 44F-40002B VENT FILTER AIR PULSING SOL VALVE OPEN COMMAND | 44HVY-4000040A
44XVYA-4000010 | 44V-40001A LINE CONVEYING GAS VALVE OPEN COMMAND | 44XVYA-4000010
44XVYB-4000010 | 44V-40001A LINE CONVEYING GAS VALVE CLOSE COMMAND | 44XVYB-4000010
44ZLSH-4000010 | 44V-40001A LINE CONVEYING GAS VALVE OPEN LIMIT SWITCH | 44ZLSH-4000010
44ZLSL-4000010 | 44V-40001A LINE CONVEYING GAS VALVE CLOSE LIMIT SWITCH | 44ZLSL-4000010
44XVYA-4000011 | 44V-40001B LINE CONVEYING GAS VALVE OPEN COMMAND | 44XVYA-4000011
44XVYB-4000011 | 44V-40001B LINE CONVEYING GAS VALVE CLOSE COMMAND | 44XVYB-4000011
44ZLSH-4000011 | 44V-40001B LINE CONVEYING GAS VALVE OPEN LIMIT SWITCH | 44ZLSH-4000011
44ZLSL-4000011 | 44V-40001B LINE CONVEYING GAS VALVE CLOSE LIMIT SWITCH | 44ZLSL-4000011
44XVYA-4000006 | 44L-40001 DEGASSING DISCHARGE DIVERTER VALVE THROUGH COMMAND | 44XVYA-4000006
44XVYB-4000006 | 44L-40001 DEGASSING DISCHARGE DIVERTER VALVE DIVERT COMMAND | 44XVYB-4000006
44ZLSH-4000006 | 44L-40001 DEGASSING DISCHARGE DIVERTER VALVE THROUGH LIMIT | 44ZLSH-4000006
44ZLSL-4000006 | 44L-40001 DEGASSING DISCHARGE DIVERTER VALVE DIVERT LIMIT | 44ZLSL-4000006
44PV-4001001A | 44C-40001A/B POWDER CONVEYING SYSTEM N2 PRESSURE CONTROL VALVE DEMAND | 44PV-4001001A
44PZLH-4001001A | 44C-40001A/B POWDER CONVEYING SYSTEM N2 PRESSURE CONTROL VALVE OPEN LIMIT SWITCH | 44PZLH-4001001A
44PZLL-4001001A | 44C-40001A/B POWDER CONVEYING SYSTEM N2 PRESSURE CONTROL VALVE CLOSE LIMIT SWITCH | 44PZLL-4001001A
44PVYA-4001001A | POWDER CONVEYING-A SYSTEM N2 SUPPLY VALVE OPEN COMMAND | 44PVYA-4001001A
44XVYB-4001001 | 44C-40001A CONVEYING GAS COMPRESSOR EQUALIZING VALVE CLOSE COMMAND | 44XVYB-4001001
44ZLSH-4001001 | 44C-40001A CONVEYING GAS COMPRESSOR VALVE OPEN LIMIT SWITCH | 44ZLSH-4001001
44ZLSL-4001001 | 44C-40001A CONVEYING GAS COMPRESSOR VALVE CLOSE LIMIT SWITCH | 44ZLSL-4001001
44XVYB-4002001 | 44C-40001B CONVEYING GAS COMPRESSOR EQUALIZING VALVE CLOSE COMMAND | 44XVYB-4002001
44ZLSH-4002001 | 44C-40001B CONVEYING GAS COMPRESSOR EQUALIZING VALVE OPEN LIMIT SWITCH | 44ZLSH-4002001
44ZLSL-4002001 | 44C-40001B CONVEYING GAS COMPRESSOR EQUALIZING VALVE CLOSE LIMIT SWITCH | 44ZLSL-4002001
44XVYA-4003016 | 44L-40002 DEODORIZING SYSTEM DIVERTER VALVE THROUGH COMMAND | 44XVYA-4003016
44XVYB-4003016 | 44L-40002 DEODORIZING SYSTEM DIVERTER VALVE DIVERT COMMAND | 44XVYB-4003016
44ZLSH-4003016 | 44L-40002 DEODORIZING SYSTEM DIVERTER VALVE THROUGH LIMIT | 44ZLSH-4003016
44ZLSL-4003016 | 44L-40002 DEODORIZING SYSTEM DIVERTER VALVE DIVERT LIMIT | 44ZLSL-4003016
44HVY-4003016 | 44S-40001A SEPARATOR N2 INLET SOL VALVE OPEN COMMAND | 44HVY-4003016
44XVY-4003005 | 44Z-40002A N2 SUPPLY SOL VALVE CLOSE COMMAND | 44XVY-4003005
44XVY-4003010 | 44Z-40003A N2 SUPPLY SOL VALVE CLOSE COMMAND | 44XVY-4003010
44HVY-4003015A | 44F-40001A SILO VENT FILTER N2 SUPPLY SOL VALVE OPEN COMMAND | 44HVY-4003015A
44XVY-4003002 | 44Z-40004A N2 SUPPLY VALVE CLOSE COMMAND | 44XVY-4003002
44XVYA-4003004 | 44Z-40002A INLET VALVE OPEN COMMAND | 44XVYA-4003004
44XVYB-4003004 | 44Z-40002A INLET VALVE CLOSE COMMAND | 44XVYB-4003004
44ZLSH-4003004 | 44Z-40002A INLET VALVE OPEN LIMIT SWITCH | 44ZLSH-4003004
44ZLSL-4003004 | 44Z-40002A INLET VALVE CLOSE LIMIT SWITCH | 44ZLSL-4003004
44XVYA-4003003 | 44D-40001A UNLOADING VALVE OPEN COMMAND | 44XVYA-4003003
44ZLSH-4003003 | 44D-40001A UNLOADING VALVE OPEN LIMIT SWITCH | 44ZLSH-4003003
44ZLSL-4003003 | 44D-40001A UNLOADING VALVE CLOSE LIMIT SWITCH | 44ZLSL-4003003
44ZLLH-4003003 | 44D-40001A UNLOADING VALVE OPEN LOCAL LAMP | 44ZLLH-4003003
44ZLLL-4003003 | 44D-40001A UNLOADING VALVE CLOSE LOCAL LAMP | 44ZLLL-4003003
44XBH-4003003 | 44D-40001A UNLOADING VALVE OPEN LOCAL SWITCH | 44XBH-4003003
44XBL-4003003 | 44D-40001A UNLOADING VALVE CLOSE LOCAL SWITCH | 44XBL-4003003
44XVYA-4003009 | 44US-40001 TRUCK UNLOADING N2 SUPPLY VALVE OPEN COMMAND | 44XVYA-4003009
44ZLSH-4003009 | 44US-40001 TRUCK UNLOADING N2 SUPPLY VALVE OPEN LIMIT SWITCH | 44ZLSH-4003009
44ZLSL-4003009 | 44US-40001 TRUCK UNLOADING N2 SUPPLY VALVE CLOSE LIMIT SWITCH | 44ZLSL-4003009
44ZLLH-4003009 | 44US-40001 TRUCK UNLOADING N2 SUPPLY VALVE OPEN LOCAL LAMP | 44ZLLH-4003009
44ZLLL-4003009 | 44US-40001 TRUCK UNLOADING N2 SUPPLY VALVE CLOSE LOCAL LAMP | 44ZLLL-4003009
44XBH-4003009 | 44US-40001 TRUCK UNLOADING N2 SUPPLY VALVE OPEN LOCAL SWITCH | 44XBH-4003009
44XBL-4003009 | 44US-40001 TRUCK UNLOADING N2 SUPPLY VALVE CLOSE LOCAL SWITCH | 44XBL-4003009
44XVYA-4003001 | 44D-40001A OUTLET VALVE OPEN COMMAND | 44XVYA-4003001
44ZLSH-4003001 | 44D-40001A OUTLET VALVE OPEN LIMIT SWITCH | 44ZLSH-4003001
44ZLSL-4003001 | 44D-40001A OUTLET VALVE CLOSE LIMIT SWITCH | 44ZLSL-4003001
44PZLH-4003055 | 44US-40001 TRUCK UNLOADING N2 SUPPLY PCV OPEN LIMIT SWITCH | 44PZLH-4003055
44PZLL-4003055 | 44US-40001 TRUCK UNLOADING N2 SUPPLY PCV CLOSE LIMIT SWITCH | 44PZLL-4003055
44XVYA-4004003 | 44D-40001B UNLOADING VALVE OPEN COMMAND | 44XVYA-4004003
44ZLSH-4004003 | 44D-40001B UNLOADING VALVE OPEN LIMIT SWITCH | 44ZLSH-4004003
44ZLSL-4004003 | 44D-40001B UNLOADING VALVE CLOSE LIMIT SWITCH | 44ZLSL-4004003
44ZLLH-4004003 | 44D-40001B UNLOADING VALVE OPEN LOCAL LAMP | 44ZLLH-4004003
44ZLLL-4004003 | 44D-40001B UNLOADING VALVE CLOSE LOCAL LAMP | 44ZLLL-4004003
44XBH-4004003 | 44D-40001B UNLOADING VALVE OPEN LOCAL SWITCH | 44XBH-4004003
44XBL-4004003 | 44D-40001B UNLOADING VALVE CLOSE LOCAL SWITCH | 44XBL-4004003
44XVYA-4004004 | 44Z-40002B INLET VALVE OPEN COMMAND | 44XVYA-4004004
44XVYB-4004004 | 44Z-40002B INLET VALVE CLOSE COMMAND | 44XVYB-4004004
44ZLSH-4004004 | 44Z-40002B INLET VALVE OPEN LIMIT SWITCH | 44ZLSH-4004004
44ZLSL-4004004 | 44Z-40002B INLET VALVE CLOSE LIMIT SWITCH | 44ZLSL-4004004
44XVYA-4004001 | 44D-40001B OUTLET VALVE OPEN COMMAND | 44XVYA-4004001
44ZLSH-4004001 | 44D-40001B OUTLET VALVE OPEN LIMIT SWITCH | 44ZLSH-4004001
44ZLSL-4004001 | 44D-40001B OUTLET VALVE CLOSE LIMIT SWITCH | 44ZLSL-4004001
44HVY-4004016 | 44S-40001B SEPARATOR N2 INLET SOL VALVE OPEN COMMAND | 44HVY-4004016
44XVY-4004005 | 44Z-40002B N2 SUPPLY SOL VALVE CLOSE COMMAND | 44XVY-4004005
44XVY-4004010 | 44Z-40003B N2 SUPPLY SOL VALVE CLOSE COMMAND | 44XVY-4004010
44HVY-4004015A | 44F-40001B SILO VENT FILTER N2 SUPPLY SOL VALVE OPEN COMMAND | 44HVY-4004015A
44XVY-4004002 | 44Z-40004B N2 SUPPLY VALVE CLOSE COMMAND | 44XVY-4004002
44XVYA-5001012 | 44L-50001A DIVERTER VALVE-A THROUGH COMMAND | 44XVYA-5001012
44XVYB-5001012 | 44L-50001A DIVERTER VALVE-A DIVERT COMMAND | 44XVYB-5001012
44ZLSH-5001012 | 44L-50001A DIVERTER VALVE-A THROUGH LIMIT | 44ZLSH-5001012
44ZLSL-5001012 | 44L-50001A DIVERTER VALVE-A DIVERT LIMIT | 44ZLSL-5001012
44XVYA-5001022 | 44L-50001B DIVERTER VALVE-B THROUGH COMMAND | 44XVYA-5001022
44XVYB-5001022 | 44L-50001B DIVERTER VALVE-B DIVERT COMMAND | 44XVYB-5001022
44ZLSH-5001022 | 44L-50001B DIVERTER VALVE-B THROUGH LIMIT | 44ZLSH-5001022
44ZLSL-5001022 | 44L-50001B DIVERTER VALVE-B DIVERT LIMIT | 44ZLSL-5001022
44XVYA-5001010 | 44L-50002 DIVERTER VALVE THROUGH COMMAND | 44XVYA-5001010
44XVYB-5001010 | 44L-50002 DIVERTER VALVE DIVERT COMMAND | 44XVYB-5001010
44ZLSH-5001010 | 44L-50002 DIVERTER VALVE THROUGH LIMIT | 44ZLSH-5001010
44ZLSL-5001010 | 44L-50002 DIVERTER VALVE DIVERT LIMIT | 44ZLSL-5001010
44XVYA-5001011 | 44WS-50005 TO 44SC-50003 VALVE OPEN COMMAND | 44XVYA-5001011
44XVYB-5001011 | 44WS-50005 TO 44SC-50003 VALVE CLOSE COMMAND | 44XVYB-5001011
44ZLSH-5001011 | 44WS-50005 TO 44SC-50003 VALVE OPEN LIMIT SWITCH | 44ZLSH-5001011
44ZLSL-5001011 | 44WS-50005 TO 44SC-50003 VALVE CLOSE LIMIT SWITCH | 44ZLSL-5001011
44XVYA-5000005 | 44WS-50002 OUTLET VALVE OPEN COMMAND | 44XVYA-5000005
44ZLSH-5000005 | 44WS-50002 OUTLET VALVE OPEN LIMIT SWITCH | 44ZLSH-5000005
44ZLSL-5000005 | 44WS-50002 OUTLET VALVE CLOSE LIMIT SWITCH | 44ZLSL-5000005
44ZLLH-5000005 | 44WS-50002 OUTLET VALVE OPEN LOCAL LAMP | 44ZLLH-5000005
44ZLLL-5000005 | 44WS-50002 OUTLET VALVE CLOSE LOCAL LAMP | 44ZLLL-5000005
44XBH-5000005 | 44WS-50002 OUTLET VALVE OPEN LOCAL SWITCH | 44XBH-5000005
44XBL-5000005 | 44WS-50002 OUTLET VALVE CLOSE LOCAL SWITCH | 44XBL-5000005
44XVYA-5000003 | 44L-50004 DIVERTER VALVE THROUGH COMMAND | 44XVYA-5000003
44XVYB-5000003 | 44L-50004 DIVERTER VALVE DIVERT COMMAND | 44XVYB-5000003
44ZLSH-5000003 | 44L-50004 DIVERTER VALVE THROUGH LIMIT | 44ZLSH-5000003
44ZLSL-5000003 | 44L-50004 DIVERTER VALVE DIVERT LIMIT | 44ZLSL-5000003
44SIC-2007019A | 44Z-20002A CONVEYING STATION SPEED CONTROLLER | 44SIC-2007019A
44SI-2007019A | 44Z-20002A CONVEYING STATION SPEED FEEDBACK | 44SI-2007019A
44SE-2007001 | 44Z-20002A CONVEYING STATION SPEED SENSOR | 44SE-2007001
44Y-2007019A-FS | 44Z-20002A CONVEYING STATION FAULT STATUS | 44Y-2007019A-FS
44Y-2007019A-PS | 44Z-20002A CONVEYING STATION STOP COMMAND | 44Y-2007019A-PS
44SIC-2007019B | 44Z-20002B CONVEYING STATION SPEED CONTROLLER | 44SIC-2007019B
44SI-2007019B | 44Z-20002B CONVEYING STATION SPEED FEEDBACK | 44SI-2007019B
44SE-2007002 | 44Z-20002B CONVEYING STATION SPEED SENSOR | 44SE-2007002
44Y-2007019B-FS | 44Z-20002B CONVEYING STATION FAULT STATUS | 44Y-2007019B-FS
44Y-2007019B-PS | 44Z-20002B CONVEYING STATION STOP COMMAND | 44Y-2007019B-PS
44SIC-4000010A | 44Z-40001A CONVEYING STATION SPEED CONTROLLER | 44SIC-4000010A
44SI-4000010A | 44Z-40001A CONVEYING STATION SPEED FEEDBACK | 44SI-4000010A
44SE-4000010A | 44Z-40001A CONVEYING STATION SPEED SENSOR | 44SE-4000010A
44Y-4000010A-FS | 44Z-40001A CONVEYING STATION FAULT STATUS | 44Y-4000010A-FS
44Y-4000010A-PS | 44Z-40001A CONVEYING STATION STOP COMMAND | 44Y-4000010A-PS
44SIC-4000010B | 44Z-40001B CONVEYING STATION SPEED CONTROLLER | 44SIC-4000010B
44SI-4000010B | 44Z-40001B CONVEYING STATION SPEED FEEDBACK | 44SI-4000010B
44SE-4000010B | 44Z-40001B CONVEYING STATION SPEED SENSOR | 44SE-4000010B
44Y-4000010B-FS | 44Z-40001B CONVEYING STATION FAULT STATUS | 44Y-4000010B-FS
44Y-4000010B-PS | 44Z-40001B CONVEYING STATION STOP COMMAND | 44Y-4000010B-PS
44Y-4001010-PA | 44C-40001A CONVEYING AIR COMPRESSOR START COMMAND | 44Y-4001010-PA
44Y-4001010-PS | 44C-40001A CONVEYING AIR COMPRESSOR STOP COMMAND | 44Y-4001010-PS
44Y-4001010-RA | 44C-40001A CONVEYING AIR COMPRESSOR LOCAL / REMOTE | 44Y-4001010-RA
44Y-4001010-RS | 44C-40001A CONVEYING AIR COMPRESSOR RUNNING STATUS | 44Y-4001010-RS
44Y-4001010-FS | 44C-40001A CONVEYING AIR COMPRESSOR FAULT STATUS | 44Y-4001010-FS
44Y-4002010-PA | 44C-40001B CONVEYING AIR COMPRESSOR START COMMAND | 44Y-4002010-PA
44Y-4002010-PS | 44C-40001B CONVEYING AIR COMPRESSOR STOP COMMAND | 44Y-4002010-PS
44Y-4002010-RA | 44C-40001B CONVEYING AIR COMPRESSOR LOCAL / REMOTE | 44Y-4002010-RA
44Y-4002010-RS | 44C-40001B CONVEYING AIR COMPRESSOR RUNNING STATUS | 44Y-4002010-RS
44Y-4002010-FS | 44C-40001B CONVEYING AIR COMPRESSOR FAULT STATUS | 44Y-4002010-FS
44SIC-4003010 | 44Z-40002A ROTARY VALVE SPEED CONTROLLER | 44SIC-4003010
44SI-4003010 | 44Z-40002A ROTARY VALVE SPEED FEEDBACK | 44SI-4003010
44SE-4003010 | 44Z-40002A ROTARY VALVE SPEED SENSOR | 44SE-4003010
44Y-4003010-FS | 44Z-40002A ROTARY VALVE FAULT STATUS | 44Y-4003010-FS
44Y-4003010-PS | 44Z-40002A ROTARY VALVE STOP COMMAND | 44Y-4003010-PS
44SIC-4003011 | 44Z-40003A ROTARY VALVE SPEED CONTROLLER | 44SIC-4003011
44SI-4003011 | 44Z-40003A ROTARY VALVE SPEED FEEDBACK | 44SI-4003011
44SE-4003011 | 44Z-40003A ROTARY VALVE SPEED SENSOR | 44SE-4003011
44Y-4003011-FS | 44Z-40003A ROTARY VALVE FAULT STATUS | 44Y-4003011-FS
44Y-4003011-PS | 44Z-40003A ROTARY VALVE STOP COMMAND | 44Y-4003011-PS
44SIC-4003012 | 44Z-40004A ROTARY VALVE SPEED CONTROLLER | 44SIC-4003012
44SI-4003012 | 44Z-40004A ROTARY VALVE SPEED FEEDBACK | 44SI-4003012
44SE-4003012 | 44Z-40004A ROTARY VALVE SPEED SENSOR | 44SE-4003012
44Y-4003012-FS | 44Z-40004A ROTARY VALVE FAULT STATUS | 44Y-4003012-FS
44Y-4003012-PS | 44Z-40004A ROTARY VALVE STOP COMMAND | 44Y-4003012-PS
44SIC-4004010 | 44Z-40002B ROTARY VALVE SPEED CONTROLLER | 44SIC-4004010
44SI-4004010 | 44Z-40002B ROTARY VALVE SPEED FEEDBACK | 44SI-4004010
44SE-4004010 | 44Z-40002B ROTARY VALVE SPEED SENSOR | 44SE-4004010
44Y-4004010-FS | 44Z-40002B ROTARY VALVE FAULT STATUS | 44Y-4004010-FS
44Y-4004010-PS | 44Z-40002B ROTARY VALVE STOP COMMAND | 44Y-4004010-PS
44SIC-4004011 | 44Z-40003B ROTARY VALVE SPEED CONTROLLER | 44SIC-4004011
44SI-4004011 | 44Z-40003B ROTARY VALVE SPEED FEEDBACK | 44SI-4004011
44SE-4004011 | 44Z-40003B ROTARY VALVE SPEED SENSOR | 44SE-4004011
44Y-4004011-FS | 44Z-40003B ROTARY VALVE FAULT STATUS | 44Y-4004011-FS
44Y-4004011-PS | 44Z-40003B ROTARY VALVE STOP COMMAND | 44Y-4004011-PS
44SIC-4004012 | 44Z-40004B ROTARY VALVE SPEED CONTROLLER | 44SIC-4004012
44SI-4004012 | 44Z-40004B ROTARY VALVE SPEED FEEDBACK | 44SI-4004012
44SE-4004012 | 44Z-40004B ROTARY VALVE SPEED SENSOR | 44SE-4004012
44Y-4004012-FS | 44Z-40004B ROTARY VALVE FAULT STATUS | 44Y-4004012-FS
44Y-4004012-PS | 44Z-40004B ROTARY VALVE STOP COMMAND | 44Y-4004012-PS
44ZSH-5001001 | XV-5001001 LIMIT SWITCH | 44ZSH-5001001
44ZSH-5001031 | XV-5001031 LIMIT SWITCH | 44ZSH-5001031
44ZSH-5001051 | XV-5001051 LIMIT SWITCH | 44ZSH-5001051