## IO_Summary
I/O SUMMARY for POWDER Transfer Package
PROJECT : 300 KT POLYETHYLENE PLANT ARYA SASOL POLYMER COMPANY (ASPC)
DESCRIPTION |  | DI | DO | AI | AO | SUM | REMARK
| POWDER (DCS) | 8 | 1 | 6 | 2 | 17
| POWDER (ESD) | 14 | 18 | 6 | 0 | 38
TOTAL |  | 22 | 19 | 12 | 2 | 55
Note.
* It's actual I/O points. The DCS/ESD System has to have 20% spare points.

## GUIDE-I
DESCRIPTION and USER'S GUIDE for IO LIST
1. General Notes
1) This list applies to measurements and devices to be monitored and controlled by the DCS.
2) For preparing the measurement List, the following format and description are to be used as guide-lines.
2. Format and guide-lines to fill out
|  | NO |  |  |  | TAG NO |  | SERVICE DESCRIPTION | FROM /TO | RANGE | UNIT | SET POINT |  |  |  | SIGNAL TYPE |  | PWR SRC | I/O TYPE |  | CONT -ACT | FUNCTION | [5 empty] | INST TYPE | IS/NIS | VALVE ACTION | LOOP TAG NO | JUNCTION BOX NO | P & ID | LOGIC / LOOP NO | REMARK
[12 empty] | LL | L | H | HH | [6 empty] | C | I | R | A | Z | SOE
|  | (1) |  |  |  | (2) |  | (3) | (4) | (5) | (6) | (7) |  |  |  | (8) |  | (9) | (10) |  | (11) | (12) | [5 empty] | (13) | (14) | (15) | (16) | (17) | (18) | (19) | (20)
(1) NO : Serial Number
(2) ID NO : Identification Number (20 digits with dash mark)
(3) SERVICE DESCRIPTION
Service description of instrument or device is specified.
(4) FROM/TO (5 digits)
"FROM" means the source of DCS input signal and "TO" means the destination of DCS output signal as follows ;
[5 empty] | FLD |  | : FIELD (OR LOCAL) | [6 empty] | BC |  |  | : BATTERY CHARGER
[5 empty] | MCC |  | : MOTOR CONTROL CENTER | [6 empty] | DG |  |  | : DIESEL GENERATOR
[5 empty] | SG |  | : SWITCHGEAR | [6 empty] | PRP |  |  | : PROTECTION RELAY PANEL
[5 empty] | LC |  | : LOAD CENTER | [6 empty] | TDP |  |  | : TRANSDUCER PANEL
[5 empty] | CCB |  | : CENTRAL CONTROL BUILDING | [6 empty] | TPP |  |  | : T/L PROTECTION PANEL
[5 empty] | LCP |  | : LOCAL CONTROL PANEL | [6 empty] | BFP |  |  | : BREAKER FAILURE PANEL
[5 empty] | EPLC |  | : ELECTRIC PROGRAMMABLE LOGIC CONTROLLER
[5 empty] | BPP |  | : BUS PROTECTION PANEL | [6 empty] | DP |  |  | : DISTRIBUTION PANEL
[5 empty] | UPS |  | : UNINTERRUPTIBLE POWER SYSTEM | [6 empty] | VR |  |  | : VOLTAGE REGULATOR SYSTEM
[5 empty] | ANN |  | : PLANT ANNUNCIATOR SYSTEM | [6 empty] | COAL |  |  | : COAL HANDLING SYSEM
[5 empty] | ELE |  | : ELECTRICAL AUX RELAY | [6 empty] | DCS |  |  | : DISTRIBUTED CONTROL SYSTEM
[5 empty] | VMS |  | : VIBRATION MONITORING SYSTEM | [6 empty] | ESD |  |  | : EMERGENCY SHUTDOWN
[5 empty] | ECMS |  | : ELECTICAL CONTROL AND MONITORING SYSTEM
[5 empty] | PTC |  | : PULSE TIMER CONTROLLER | [6 empty] | MCC-VFD |  |  | : Variable frequency drive located in substation
[5 empty] | LCS |  | : LOCAL CONTROL STATION | [6 empty] | RLY |  |  | : INTERPOSING RELAY CABINET
(5) RANGE (20 digits)
Process variable range is specified.(for example 300 ~ 10,000)
(6) UNIT (8 digits)
The engineering units used in this list are as follows ;
[7 empty] | ORIGINAL UNIT |  | DESCRIPTION USED | [7 empty] | ORIGINAL UNIT |  |  | DESCRIPTION USED
[7 empty] | bar gage |  | bar.g (mbar.g) | [7 empty] | Megawatt |  |  | MW
[7 empty] | Vacuum |  | mbar.a | [7 empty] | Hertz |  |  | Hz, KHz
[7 empty] | ℃ (Degree C) |  | ℃ | [7 empty] | Percent |  |  | %
[7 empty] | millimeter, inch |  | MM, IN | [7 empty] | micro mho/Cm |  |  | UMHO
[7 empty] | Meter |  | M | [7 empty] | kcal/hour |  |  | KC/H
[7 empty] | part(s) per million |  | PPM | [7 empty] | revolution per minute |  |  | RPM
[7 empty] | part(s) per billion |  | PPB | [7 empty] | Ton/Hour |  |  | T/H
[7 empty] | pH |  | PH | [7 empty] | kg/hour |  |  | KG/H
[7 empty] | Volt |  | V | [7 empty] | liter/minute |  |  | L/M
[7 empty] | Kilovolt |  | KV
[7 empty] | Ampere |  | A
(7) SET POINT
This column shows the software threshold value in analog input for alarm or interlock purpose.
- HH : High-High Alarming
- H : High Alarming
- L : Low Alarming
- LL : Low-Low Alarming
(8) SIGNAL TYPE (6 digits)
The type of input/output signal is specified as follows ;
|  |  |  | 4~20mA |  |  | : 4-20 mA with HART protocol
|  |  |  | NAMUR |  |  | : NAMUR for proximity switches
|  |  |  | 24V DC |  |  | : 24V DC binary signals
|  |  |  | VFC |  |  | : Volt Free Contact
(9) PWR SRC : Power source (1 digit)
The power source of signal is specified as follows ;
|  |  |  | . I |  |  | : INTERNAL POWER SUPPLIED FROM DCS
|  |  |  | . E |  |  | : EXTERNAL POWER SUPPLIED FROM OUTSIDE OF DCS
(10) I/O TYPE ( 2 digits)
The signal type of input or output is specified as follows :
|  |  |  | . AI |  |  | : ANALOG INPUT
|  |  |  | . AO |  |  | : ANALOG OUTPUT
|  |  |  | . DI |  |  | : DIGITAL INPUT
|  |  |  | . DO |  |  | : DIGITAL OUTPUT
(11) CONTACT : Contact type (2 digits)
The status of digital contact is specified when the equipment is de-energized, closed or stopped etc.
|  |  |  | . NO |  |  | : NORMALLY OPEN CONTACT
|  |  |  | . NC |  |  | : NORMALLY CLOSED CONTACT
(12) FUNCTION
The function of I/O Signal is marked in appropriate column. This column shows variable function displayed on LED of DCS.
The Function on this column refers as follows;
- C : Controlling
- I : Indicating
- R : Recording or Trending
- A : Alarm
- Z : Plant Protection
- SOE : Sequence of Event
(13) INST TYPE
The description of Tag No.
(14) IS/NIS
The Ex. Protection types
(15) VALVE ACTION
Valve action(Fail Position) is specified.
(16) LOOP TAG NO.
Loop tag number is specified.
(17) JUNCTION BOX NO.
Junction box number is specified.
(18) P & ID NO.
P&ID drawing number is specified.
(19) LOGIC / LOOP NO.
Logic/Loop drawing number is specified.
(20) REMARK
Additional information is described.

## Powder_IO (DCS)
[9 empty] | PROJECT NO. : 3944 | IO LIST (DCS) FOR POWDER TRANSFER PACKAGE
MR NO. : 171
DOC TITLE : IO LIST (POWDER)
DOC NO. : 3944-VD-0171-DYP-RE-400-LST-0080
REV : 01
| NO | TAG NO. | [6 empty] | SERVICE DESCRIPTION | FROM /TO | RANGE | UNIT | SET-POINT |  |  |  | SIGNAL TYPE | PWR SRC | I/O TYPE | CONT -ACT | FUNCTION | [5 empty] | INST TYPE | IS / NIS | VALVE ACTION | LOOP TAG NO. | JUNCTION BOX NO. | P&ID NO. | LOGIC NO. (3944-VD-0171-DYP-RE-400-DIA-0083 Sh.NNN) | REMARK | DI | DO | AI | AO | SUM
for Sort | [12 empty] | LL | L | H | HH |  |  |  |  | C | I | R | A | Z | SOE | [8 empty] | 8 | 1 | 6 | 2 | 17
- | Instruments
- | 1 | 44 | FT | - | 20070 | 60 |  |  | POWDER CONVEYING N2 SUPPLY FLOW | FLD / DCS | 0~600 | Nm3/h | - | 450 | - | - | 4~20mA | I | AI | - |  | O |  | O |  |  | FLOW TRANSMITTER DP-INTEGRAL ORIFICE | IS | - | by other | by other | 20070 | LATER
- | 2 | 44 | PT | - | 20070 | 62 |  |  | POWDER CONVEYING N2 SUPPLY PRESSURE | FLD / DCS | 0~6 | bar.g | 3 | 3.5 | 4.5 | 5 | 4~20mA | I | AI | - |  | O |  | O |  |  | PRESSURE TRANSMITTER | IS | - | by other | by other | 20070 | LATER
- | 3 | 44 | PT | - | 20070 | 19 |  |  | 44Z-20002A CONVEYING STATION PURGING PRESSURE | FLD / DCS | 0~5 | bar.g | - | 1.8 | - | - | 4~20mA | I | AI | - |  | O |  | O |  |  | PRESSURE TRANSMITTER | IS | - | by other | by other | 20070 | LATER
- | 4 | 44 | PT | - | 20070 | 20 |  |  | 44Z-20002B CONVEYING STATION PURGING PRESSURE | FLD / DCS | 0~5 | bar.g | - | 1.8 | - | - | 4~20mA | I | AI | - |  | O |  | O |  |  | PRESSURE TRANSMITTER | IS | - | by other | by other | 20070 | LATER
- | 5 | 44 | PDT | - | 20070 | 03 |  |  | 44F-20002 VENT FILTER DIFF. PRESSURE | FLD / DCS | 0~500 | mmH2O | - | - | 300 | - | 4~20mA | I | AI | - |  | O |  | O |  |  | DIFF PRESSURE TRANSMITTER | IS | - | by other | by other | 20070 | LATER
- | 6 | 44 | LSH | - | 20070 | 03A |  |  | 44V-20001A BLOW TANK LEVEL HIGH SWITCH | FLD / DCS | - | - | - | - | - | - | 24V DC | I | DI | NO |  | O |  | O |  |  | LEVEL SWITCH HIGH | IS | - | by other | by other | 20070 | LATER | ADD_R1
- | 7 | 44 | LSL | - | 20070 | 02A |  |  | 44V-20001A BLOW TANK LEVEL LOW SWITCH | FLD / DCS | - | - | - | - | - | - | 24V DC | I | DI | NO |  | O |  | O |  |  | LEVEL SWITCH LOW | IS | - | by other | by other | 20070 | LATER | ADD_R1
- | 8 | 44 | LSH | - | 20070 | 03B |  |  | 44V-20001B BLOW TANK LEVEL HIGH SWITCH | FLD / DCS | - | - | - | - | - | - | 24V DC | I | DI | NO |  | O |  | O |  |  | LEVEL SWITCH HIGH | IS | - | by other | by other | 20070 | LATER | ADD_R1
- | 9 | 44 | LSL | - | 20070 | 02B |  |  | 44V-20001B BLOW TANK LEVEL LOW SWITCH | FLD / DCS | - | - | - | - | - | - | 24V DC | I | DI | NO |  | O |  | O |  |  | LEVEL SWITCH LOW | IS | - | by other | by other | 20070 | LATER | ADD_R1
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
-
- | Valves
XV-2007005 | 1 | 44 | XVYA | - | 20070 | 05 |  |  | POWDER CONVEYING N2 SUPPLY VALVE OPEN COMMAND | DCS / FLD | - | - | - | - | - | - | 24V DC | I | DO | - | O | [5 empty] | SOLENOID VALVE | NIS | FAIL CLOSE | by other | by other | 20070 | LATER
XV-2007005 | 2 | 44 | ZLSH | - | 20070 | 05 |  |  | POWDER CONVEYING N2 SUPPLY VALVE OPEN LIMIT SWITCH | FLD / DCS | - | - | - | - | - | - | NAMUR | I | DI | NO |  | O |  |  |  |  | LIMIT SWITCH-OPEN | IS | FAIL CLOSE | by other | by other | 20070 | LATER
XV-2007005 | 3 | 44 | ZLSL | - | 20070 | 05 |  |  | POWDER CONVEYING N2 SUPPLY VALVE CLOSE LIMIT SWITCH | FLD / DCS | - | - | - | - | - | - | NAMUR | I | DI | NO |  | O |  |  |  |  | LIMIT SWITCH-CLOSE | IS | FAIL CLOSE | by other | by other | 20070 | LATER
FV-2007060 | 4 | 44 | FV | - | 20070 | 60 |  |  | POWDER CONVEYING N2 SUPPLY FLOW CONTROL VALVE DEMAND | DCS / FLD | 0~100 | % | - | - | - | - | 4~20mA | I | AO | - | O | [5 empty] | POSITIONER | IS | FAIL CLOSE | by other | by other | 20070 | LATER
- | Motor, Others
44Z-20002A | 1 | 44 | SIC | - | 20070 | 19A |  |  | 44Z-20002A CONVEYING STATION SPEED CONTROLLER | DCS / MCC-VFD | 0~19.4 | RPM | - | - | - | - | 4~20mA | I | AO | - | O | [5 empty] | MOTOR SPEED DEMAND | NIS | - | by other | by other | 20070 | LATER
44Z-20002A | 2 | 44 | SI | - | 20070 | 19A |  |  | 44Z-20002A CONVEYING STATION SPEED FEEDBACK | MCC-VFD / DCS | 0~19.4 | RPM | - | - | - | - | 4~20mA | I | AI | - |  | O |  |  |  |  | MOTOR SPEED FEEDBACK | NIS | - | by other | by other | 20070 | LATER
44Z-20002A | 3 | 44 | SE | - | 20070 | 01 |  |  | 44Z-20002A CONVEYING STATION SPEED SENSOR | FLD / DCS | - | - | - | - | - | - | 24V DC | I | DI | NO |  | O |  | O |  |  | MOTOR SPEED SENSOR | NIS | - | by other | by other | 20070 | LATER
44Z-20002A | 4 | 44 | Y | - | 20070 | 19A | - | FS | 44Z-20002A CONVEYING STATION FAULT STATUS | EPLC / DCS | - | - | - | - | - | - | 24V DC | I | DI | NO |  | O |  | O |  |  | MOTOR FAULT STATUS | NIS | - | by other | by other | 20070 | LATER

## Powder_IO (ESD)
[9 empty] | PROJECT NO. : 3944 | IO LIST (ESD) FOR POWDER TRANSFER PACKAGE
MR NO. : 171
DOC TITLE : IO LIST (POWDER)
DOC NO. : 3944-VD-0171-DYP-RE-400-LST-0080
REV : 01
| NO | TAG NO. | [6 empty] | SERVICE DESCRIPTION | FROM /TO | RANGE | UNIT | SET-POINT |  |  |  | SIGNAL TYPE | PWR SRC | I/O TYPE | CONT -ACT | FUNCTION | [5 empty] | INST TYPE | IS / NIS | VALVE ACTION | LOOP TAG NO. | JUNCTION BOX NO. | P&ID NO. | LOGIC NO. (3944-VD-0171-DYP-RE-400-DIA-0083 Sh.NNN) | REMARK | DI | DO | AI | AO | SUM
[13 empty] | LL | L | H | HH |  |  |  |  | C | I | R | A | Z | SOE | [8 empty] | 14 | 18 | 6 | 0 | 38
- | Instruments
- | 1 | 44 | PT | - | 20070 | 06A |  |  | 44V-20001A BLOW TANK PRESSURE-1 (1 of 2) | FLD / ESD | 0~15 | bar.g | - | 7 | 10 | 12 | 4~20mA | I | AI | - |  | O |  | O |  |  | PRESSURE TRANSMITTER | IS | - | by other | by other | 20070 | LATER
- | 2 | 44 | PT | - | 20070 | 07A |  |  | 44V-20001A BLOW TANK PRESSURE-2 (1 of 2) | FLD / ESD | 0~15 | bar.g | - | - | 10 | - | 4~20mA | I | AI | - |  | O |  | O |  |  | PRESSURE TRANSMITTER | IS | - | by other | by other | 20070 | LATER
- | 3 | 44 | PT | - | 20070 | 06B |  |  | 44V-20001B BLOW TANK PRESSURE-1 (1 of 2) | FLD / ESD | 0~15 | bar.g | - | 7 | 10 | 12 | 4~20mA | I | AI | - |  | O |  | O |  |  | PRESSURE TRANSMITTER | IS | - | by other | by other | 20070 | LATER
- | 4 | 44 | PT | - | 20070 | 07B |  |  | 44V-20001B BLOW TANK PRESSURE-2 (1 of 2) | FLD / ESD | 0~15 | bar.g | - | - | 10 | - | 4~20mA | I | AI | - |  | O |  | O |  |  | PRESSURE TRANSMITTER | IS | - | by other | by other | 20070 | LATER
- | 5 | 44 | PT | - | 20070 | 04 |  |  | POWDER TO 44R-20001 TRANSFER PRESSURE-1 (1 of 2) | FLD / ESD | 0~15 | bar.g | - | - | 10 | 12 | 4~20mA | I | AI | - |  | O |  | O |  |  | PRESSURE TRANSMITTER | IS | - | by other | by other | 20070 | LATER
- | 6 | 44 | PT | - | 20070 | 05 |  |  | POWDER TO 44R-20001 TRANSFER PRESSURE-2 (1 of 2) | FLD / ESD | 0~15 | bar.g | - | - | 10 | 12 | 4~20mA | I | AI | - |  | O |  | O |  |  | PRESSURE TRANSMITTER | IS | - | by other | by other | 20070 | LATER
-
- | Valves
XV-2007017 | 1 | 44 | XVYA | - | 20070 | 17 |  |  | 44TK-20002A/B TO BLOW TANK VALVE-1 OPEN COMMAND | ESD / FLD | - | - | - | - | - | - | 24V DC | I | DO | - | O | [5 empty] | SOLENOID VALVE | NIS | FAIL CLOSE | by other | by other | 20070 | LATER
XV-2007017 | 2 | 44 | ZLSH | - | 20070 | 17 |  |  | 44TK-20002A/B TO BLOW TANK VALVE-1 OPEN LIMIT SWITCH | FLD / ESD | - | - | - | - | - | - | NAMUR | I | DI | NO |  | O |  |  |  |  | LIMIT SWITCH-OPEN | IS | FAIL CLOSE | by other | by other | 20070 | LATER
XV-2007017 | 3 | 44 | ZLSL | - | 20070 | 17 |  |  | 44TK-20002A/B TO BLOW TANK VALVE-1 CLOSE LIMIT SWITCH | FLD / ESD | - | - | - | - | - | - | NAMUR | I | DI | NO |  | O |  |  |  |  | LIMIT SWITCH-CLOSE | IS | FAIL CLOSE | by other | by other | 20070 | LATER
XV-2007014 | 4 | 44 | XVYA | - | 20070 | 14 |  |  | 44TK-20002A/B TO BLOW TANK VALVE-2 OPEN COMMAND | ESD / FLD | - | - | - | - | - | - | 24V DC | I | DO | - | O | [5 empty] | SOLENOID VALVE | NIS | FAIL CLOSE | by other | by other | 20070 | LATER
XV-2007014 | 5 | 44 | ZLSH | - | 20070 | 14 |  |  | 44TK-20002A/B TO BLOW TANK VALVE-2 OPEN LIMIT SWITCH | FLD / ESD | - | - | - | - | - | - | NAMUR | I | DI | NO |  | O |  |  |  |  | LIMIT SWITCH-OPEN | IS | FAIL CLOSE | by other | by other | 20070 | LATER
XV-2007014 | 6 | 44 | ZLSL | - | 20070 | 14 |  |  | 44TK-20002A/B TO BLOW TANK VALVE-2 CLOSE LIMIT SWITCH | FLD / ESD | - | - | - | - | - | - | NAMUR | I | DI | NO |  | O |  |  |  |  | LIMIT SWITCH-CLOSE | IS | FAIL CLOSE | by other | by other | 20070 | LATER
XV-2007042 | 7 | 44 | XVYA | - | 20070 | 42 |  |  | 44V-20001A BLOW TANK VENT VALVE OPEN COMMAND | ESD / FLD | - | - | - | - | - | - | 24V DC | I | DO | - | O | [5 empty] | SOLENOID VALVE | NIS | FAIL CLOSE | by other | by other | 20070 | LATER
XV-2007042 | 8 | 44 | ZLSH | - | 20070 | 42 |  |  | 44V-20001A BLOW TANK VENT VALVE OPEN LIMIT SWITCH | FLD / ESD | - | - | - | - | - | - | NAMUR | I | DI | NO |  | O |  |  |  |  | LIMIT SWITCH-OPEN | IS | FAIL CLOSE | by other | by other | 20070 | LATER
XV-2007042 | 9 | 44 | ZLSL | - | 20070 | 42 |  |  | 44V-20001A BLOW TANK VENT VALVE CLOSE LIMIT SWITCH | FLD / ESD | - | - | - | - | - | - | NAMUR | I | DI | NO |  | O |  |  |  |  | LIMIT SWITCH-CLOSE | IS | FAIL CLOSE | by other | by other | 20070 | LATER
XV-2007010 | 10 | 44 | XVYA | - | 20070 | 10 |  |  | 44V-20001A OUTLET VALVE OPEN COMMAND | ESD / FLD | - | - | - | - | - | - | 24V DC | I | DO | - | O | [5 empty] | SOLENOID VALVE | NIS | FAIL CLOSE | by other | by other | 20070 | LATER
XV-2007010 | 11 | 44 | ZLSH | - | 20070 | 10 |  |  | 44V-20001A OUTLET VALVE OPEN LIMIT SWITCH | FLD / ESD | - | - | - | - | - | - | NAMUR | I | DI | NO |  | O |  |  |  |  | LIMIT SWITCH-OPEN | IS | FAIL CLOSE | by other | by other | 20070 | LATER
XV-2007010 | 12 | 44 | ZLSL | - | 20070 | 10 |  |  | 44V-20001A OUTLET VALVE CLOSE LIMIT SWITCH | FLD / ESD | - | - | - | - | - | - | NAMUR | I | DI | NO |  | O |  |  |  |  | LIMIT SWITCH-CLOSE | IS | FAIL CLOSE | by other | by other | 20070 | LATER
XV-2007012 | 13 | 44 | XVYA | - | 20070 | 12 |  |  | 44V-20001B OUTLET VALVE-1 OPEN COMMAND | ESD / FLD | - | - | - | - | - | - | 24V DC | I | DO | - | O | [5 empty] | SOLENOID VALVE | NIS | FAIL CLOSE | by other | by other | 20070 | LATER
XV-2007012 | 14 | 44 | ZLSH | - | 20070 | 12 |  |  | 44V-20001B OUTLET VALVE-1 OPEN LIMIT SWITCH | FLD / ESD | - | - | - | - | - | - | NAMUR | I | DI | NO |  | O |  |  |  |  | LIMIT SWITCH-OPEN | IS | FAIL CLOSE | by other | by other | 20070 | LATER
XV-2007012 | 15 | 44 | ZLSL | - | 20070 | 12 |  |  | 44V-20001B OUTLET VALVE-1 CLOSE LIMIT SWITCH | FLD / ESD | - | - | - | - | - | - | NAMUR | I | DI | NO |  | O |  |  |  |  | LIMIT SWITCH-CLOSE | IS | FAIL CLOSE | by other | by other | 20070 | LATER
XV-2007013 | 16 | 44 | XVYA | - | 20070 | 13 |  |  | 44V-20001B OUTLET VALVE-2 OPEN COMMAND | ESD / FLD | - | - | - | - | - | - | 24V DC | I | DO | - | O | [5 empty] | SOLENOID VALVE | NIS | FAIL CLOSE | by other | by other | 20070 | LATER
XV-2007013 | 17 | 44 | ZLSH | - | 20070 | 13 |  |  | 44V-20001B OUTLET VALVE-2 OPEN LIMIT SWITCH | FLD / ESD | - | - | - | - | - | - | NAMUR | I | DI | NO |  | O |  |  |  |  | LIMIT SWITCH-OPEN | IS | FAIL CLOSE | by other | by other | 20070 | LATER
XV-2007013 | 18 | 44 | ZLSL | - | 20070 | 13 |  |  | 44V-20001B OUTLET VALVE-2 CLOSE LIMIT SWITCH | FLD / ESD | - | - | - | - | - | - | NAMUR | I | DI | NO |  | O |  |  |  |  | LIMIT SWITCH-CLOSE | IS | FAIL CLOSE | by other | by other | 20070 | LATER
XV-2007011 | 19 | 44 | XVYA | - | 20070 | 11 |  |  | 44V-20001A/B TIE VALVE OPEN COMMAND | ESD / FLD | - | - | - | - | - | - | 24V DC | I | DO | - | O | [5 empty] | SOLENOID VALVE | NIS | FAIL CLOSE | by other | by other | 20070 | LATER
XV-2007011 | 20 | 44 | ZLSH | - | 20070 | 11 |  |  | 44V-20001A/B TIE VALVE VALVE OPEN LIMIT SWITCH | FLD / ESD | - | - | - | - | - | - | NAMUR | I | DI | NO |  | O |  |  |  |  | LIMIT SWITCH-OPEN | IS | FAIL CLOSE | by other | by other | 20070 | LATER
XV-2007011 | 21 | 44 | ZLSL | - | 20070 | 11 |  |  | 44V-20001A/B TIE VALVE VALVE CLOSE LIMIT SWITCH | FLD / ESD | - | - | - | - | - | - | NAMUR | I | DI | NO |  | O |  |  |  |  | LIMIT SWITCH-CLOSE | IS | FAIL CLOSE | by other | by other | 20070 | LATER
-
- | Motors
- | 1 | 44 | Y | - | 20070 | 19A | - | ES | 44Z-20002A CONVEYING STATION EMERGENCY STOP COMMAND | ESD / EPLC | - | - | - | - | - | - | 24V DC | E | DO | - | O | [5 empty] | MOTOR STOP CMD | NIS | - | by other | by other | 20070 | LATER
- | 2 | 44 | Y | - | 20070 | 19B | - | ES | 44Z-20002B CONVEYING STATION EMERGENCY STOP COMMAND | ESD / EPLC | - | - | - | - | - | - | 24V DC | E | DO | - | O | [5 empty] | MOTOR STOP CMD | NIS | - | by other | by other | 20070 | LATER
- | 3 | 44 | Y | - | 40000 | 10A | - | ES | 44Z-40001A CONVEYING STATION EMERGENCY STOP COMMAND | ESD / EPLC | - | - | - | - | - | - | 24V DC | E | DO | - | O | [5 empty] | MOTOR STOP CMD | NIS | - | by other | by other | 40000 | LATER
- | 4 | 44 | Y | - | 40000 | 10B | - | ES | 44Z-40001B CONVEYING STATION EMERGENCY STOP COMMAND | ESD / EPLC | - | - | - | - | - | - | 24V DC | E | DO | - | O | [5 empty] | MOTOR STOP CMD | NIS | - | by other | by other | 40000 | LATER
- | 5 | 44 | Y | - | 40030 | 10A | - | ES | 44Z-40002A ROTARY VALVE EMERGENCY STOP COMMAND | ESD / EPLC | - | - | - | - | - | - | 24V DC | E | DO | - | O | [5 empty] | MOTOR STOP CMD | NIS | - | by other | by other | 40030 | LATER
- | 6 | 44 | Y | - | 40030 | 11A | - | ES | 44Z-40003A ROTARY VALVE EMERGENCY STOP COMMAND | ESD / EPLC | - | - | - | - | - | - | 24V DC | E | DO | - | O | [5 empty] | MOTOR STOP CMD | NIS | - | by other | by other | 40030 | LATER
- | 7 | 44 | Y | - | 40030 | 12A | - | ES | 44Z-40004A ROTARY VALVE EMERGENCY STOP COMMAND | ESD / EPLC | - | - | - | - | - | - | 24V DC | E | DO | - | O | [5 empty] | MOTOR STOP CMD | NIS | - | by other | by other | 40030 | LATER
- | 8 | 44 | Y | - | 40040 | 10A | - | ES | 44Z-40002B ROTARY VALVE EMERGENCY STOP COMMAND | ESD / EPLC | - | - | - | - | - | - | 24V DC | E | DO | - | O | [5 empty] | MOTOR STOP CMD | NIS | - | by other | by other | 40040 | LATER
- | 9 | 44 | Y | - | 40040 | 11A | - | ES | 44Z-40003B ROTARY VALVE EMERGENCY STOP COMMAND | ESD / EPLC | - | - | - | - | - | - | 24V DC | E | DO | - | O | [5 empty] | MOTOR STOP CMD | NIS | - | by other | by other | 40040 | LATER
- | 10 | 44 | Y | - | 40040 | 12A | - | ES | 44Z-40004B ROTARY VALVE EMERGENCY STOP COMMAND | ESD / EPLC | - | - | - | - | - | - | 24V DC | E | DO | - | O | [5 empty] | MOTOR STOP CMD | NIS | - | by other | by other | 40040 | LATER
- | 11 | 44 | Y | - | 50010 | 52 | - | ES | 44C-50008 EXHAUST FAN EMERGENCY STOP COMMAND | ESD / EPLC | - | - | - | - | - | - | 24V DC | E | DO | - | O | [5 empty] | MOTOR STOP CMD | NIS | - | by other | by other | 50010 | LATER | ADD_R1