## I-4001
I-4001 POWDER TRANSFER PACKAGE Powder Pneumatic Transport | [5 empty] | EFFECT | NOTES | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
[7 empty] | ACTIVATED INTERLOCK NO. | I-4001 | I-4001 | I-4001 | I-4001 | I-4001 | I-4001 | I-4001 | I-4001 | I-4001 | I-4001 | I-4001 | I-4001 | I-4001 | I-4001 | I-4001 | I-4001 | I-4001 | I-4001
[7 empty] | SERVICE DESCRIPTION | 44V-40001A INLET KNIFE GATE CLOSE COMAND | 44Z-40001A CONVEYING STATION STOP COMMAND | 44Z-40001A PURGING SOL VALVE CLOSE COMMAND | 44Z-40001A OUTLET VALVE CLOSE COMAND | 44V-40001B INLET KNIFE GATE CLOSE COMAND | 44Z-40001B CONVEYING STATION STOP COMMAND | 44Z-40001B PURGING SOL VALVE CLOSE COMMAND | 44Z-40001B OUTLET VALVE CLOSE COMAND | 44Z-40003A N2 SUPPLY SOL VALVE CLOSE COMMAND | 44Z-40002A N2 SUPPLY SOL VALVE CLOSE COMMAND | 44Z-40002A INLET VALVE CLOSE COMMAND | 44Z-40002A ROTARY VALVE STOP COMMAND | 44Z-40003A ROTARY VALVE STOP COMMAND | 44Z-40003B N2 SUPPLY SOL VALVE CLOSE COMMAND | 44Z-40002B N2 SUPPLY SOL VALVE CLOSE COMMAND | 44Z-40002B INLET VALVE CLOSE COMMAND | 44Z-40002B ROTARY VALVE STOP COMMAND | 44Z-40003B ROTARY VALVE STOP COMMAND | LEGEND :
P - PERMISSIVE
O - OPEN OR START
C - CLOSE
S - STOP OR SHUTDOWN
A - ACTIVE
OC - OPEN CLOSE
ALM : ALARM
SI : SIGNALING AND INDICATION
DT : DELAY TIME
R : RESET
D : DEACTIVATION
[7 empty] | TAG NO. EQ'T NO. | 44XVYB-4000001 44XV-4000001 | 44Y-4000010A-PS 44Z-40001A | 44XVY-4000008 44XVY-4000008 | 44XVYB-4000016 44XV-4000016 | 44XVYB-4000002 44XV-4000002 | 44Y-4000010B-PS 44Z-40001B | 44XVY-4000009 44XVY-4000009 | 44XVYB-4000017 44XV-4000017 | 44XVY-4003010 44XVY-4003010 | 44XVY-4003005 44XVY-4003005 | 44XVYB-4003004 44XV-4003004 | 44Y-4003010-PS 44Z-40002A | 44Y-4003011-PS 44Z-40003A | 44XVY-4004010 44XVY-4004010 | 44XVY-4004005 44XVY-4004005 | 44XVYB-4004004 44XV-4004004 | 44Y-4004010-PS 44Z-40002B | 44Y-4004011-PS 44Z-40003B | (a) : 44Z-40001A Selected (b) : 44Z-40001B Selected
[7 empty] | P&ID | 40000 | 40000 | 40000 | 40000 | 40000 | 40000 | 40000 | 40000 | 40030 | 40030 | 40030 | 40030 | 40030 | 40040 | 40040 | 40040 | 40040 | 40040 | NOTES :
CAUSE | [25 empty] | 1. ALL INSTRUMENT TAG NUMBERS SHALL BE PROVIDED WITH THE UNIT NUMBER (44) UNLESS INDICATED OTHER WISE
UNIT | P&ID | TAG NO. (TRIP INITIATOR) | SERVICE DESCRIPTION | INTERLOCK NO. | NOTES |  | ITEM | [18 empty] | 2. POWDER TRANSFER PACKAGE IS CONTROLLED BY DCS
400 | 40000 | 44ZSH-4000010 | 44V-40001A LINE CONVEYING GAS VALVE OPEN FAULT POSITION DURING OPERATION | I-4001 | 2,3 |  |  | C | S | C | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 3. VALVE POSITION FAULT ALARM (DELAY TIME = 5 ~ 10 SECS)
400 | 40000 | 44ZSH-4000011 | 44V-40001B LINE CONVEYING GAS VALVE OPEN FAULT POSITION DURING OPERATION | I-4001 | 2,3 |  |  | - | - | - | - | C | S | C | C | - | - | - | - | - | - | - | - | - | -
400 | 40000 | 44ZSH-4000014 | 44V-40001A FEED HOPPER OUTLET MANUAL VALVE OPEN LIMIT SWITCH (NOT) | I-4001 | 2,3 |  |  | - | S | C | C | - | - | - | - | - | - | - | - | - | - | - | - | - | -
400 | 40000 | 44ZSH-4000016 | 44Z-40001A OUTLET VALVE OPEN FAULT POSITION DURING OPERATION | I-4001 | 2,3 |  |  | - | S | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
400 | 40000 | 44ZSH-4000015 | 44V-40001B FEED HOPPER OUTLET MANUAL VALVE OPEN LIMIT SWITCH (NOT) | I-4001 | 2,3 |  |  | - | - | - | - | - | S | C | C | - | - | - | - | - | - | - | - | - | -
400 | 40000 | 44ZSH-4000017 | 44Z-40001B OUTLET VALVE OPEN FAULT POSITION DURING OPERATION | I-4001 | 2,3 |  |  | - | - | - | - | - | S | C | - | - | - | - | - | - | - | - | - | - | -
400 | 40030 | 44ZSH-4003004 | 44Z-40002A INLET VALVE OPEN FAULT POSITION DURING OPERATION | I-4001 | 2,3 |  |  | - | S(a) | C(a) | C(a) | - | S(b) | C(b) | C(b) | C | C | - | S | S | - | - | - | - | - | 4. RUN FAULT
400 | 40040 | 44ZSH-4004004 | 44Z-40002B INLET VALVE OPEN FAULT POSITION DURING OPERATION | I-4001 | 2,3 |  |  | - | S(a) | C(a) | C(a) | - | S(b) | C(b) | C(b) | - | - | - | - | - | C | C | - | S | S | 1) WHEN AUTO OPERATING, RUNNING STATUS SIGNAL TURN OFF
400 | 40000 | 44ZSH-4000006 44ZSL-4000006 | 44L-40001 DEGASSING DISCHARGE DIVERTER VALVE THROUGH/DIVERT LIMIT SWITCH POSITION FAULT | I-4001 | 2,3 |  |  | C | S | C | C | C | S | C | C | - | - | - | - | - | - | - | - | - | - | 2) WHEN START COMMAND SIGNAL ACTIVATING,
400 | 40030 | 44ZSH-4003016 44ZSL-4003016 | 44L-40002 DEODORIZING SYSTEM DIVERTER VALVE THROUGH/DIVERT LIMIT SWITCH POSITION FAULT | I-4001 | 2,3 |  |  | C | S | C | C | C | S | C | C | - | - | - | - | - | - | - | - | - | - | RUNNING STATUS SIGNAL WILL NOT ACTIVATE FOR FEW SECONDS
400 | 40000 | 44Y-4000010A-RS | 44Z-40001A CONVEYING STATION NOT RUNNING DURING OPERATION | I-4001 | 2,4 |  |  | - | - | C | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CAUSE & EFFECT DIAGRAM FOR
400 | 40000 | 44Y-4000010B-RS | 44Z-40001B CONVEYING STATION NOT RUNNING DURING OPERATION | I-4001 | 2,4 |  |  | - | - | - | - | - | - | C | C | - | - | - | - | - | - | - | - | - | - | I-4001 POWDER TRANSFER PACKAGE Powder Pneumatic Transport
400 | 40030 | 44Y-4003010-RS | 44Z-40002A ROTARY VALVE NOT RUNNING DURING OPERATION | I-4001 | 2,4 |  |  | - | S(a) | C(a) | C(a) | - | S(b) | C(b) | C(b) | C | C | C | - | S | - | - | - | - | -
400 | 40030 | 44Y-4003011-RS | 44Z-40003A ROTARY VALVE NOT RUNNING DURING OPERATION | I-4001 | 2,4 |  |  | - | S(a) | C(a) | C(a) | - | S(b) | C(b) | C(b) | C | C | C | S | - | - | - | - | - | -
400 | 40040 | 44Y-4004010-RS | 44Z-40002B ROTARY VALVE NOT RUNNING DURING OPERATION | I-4001 | 2,4 |  |  | - | S(a) | C(a) | C(a) | - | S(b) | C(b) | C(b) | - | - | - | - | - | C | C | C | - | S
400 | 40040 | 44Y-4004011-RS | 44Z-40003B ROTARY VALVE NOT RUNNING DURING OPERATION | I-4001 | 2,4 |  |  | - | S(a) | C(a) | C(a) | - | S(b) | C(b) | C(b) | - | - | - | - | - | C | C | C | S | -
[26 empty] | PROJECT NAME | DRAWING NO | SHEET | REV
[26 empty] | PROJECT | 3944-VD-0171-DYP-RE-400-DIA-0082 | 8 | 0

## I-4101
I-4101 POWDER TRANSFER PACKAGE 44C-40001A Protection | [5 empty] | EFFECT | NOTES
ACTIVATED INTERLOCK NO.
[7 empty] | SERVICE DESCRIPTION | LEGEND :
P - PERMISSIVE
O - OPEN OR START
C - CLOSE
S - STOP OR SHUTDOWN
A - ACTIVE
OC - OPEN CLOSE
ALM : ALARM
SI : SIGNALING AND INDICATION
DT : DELAY TIME
R : RESET
D : DEACTIVATION
[7 empty] | TAG NO. EQ'T NO. | (a) : 44Z-40001A Selected (b) : 44Z-40001B Selected
[7 empty] | P&ID | NOTES :
CAUSE | [7 empty] | 1. ALL INSTRUMENT TAG NUMBERS SHALL BE PROVIDED WITH THE UNIT NUMBER (44) UNLESS INDICATED OTHER WISE
UNIT | P&ID | TAG NO. (TRIP INITIATOR) | SERVICE DESCRIPTION | INTERLOCK NO. | NOTES |  | ITEM | 2. POWDER TRANSFER PACKAGE IS CONTROLLED BY DCS
3. VALVE POSITION FAULT ALARM (DELAY TIME = 5 ~ 10 SECS)
4. RUN FAULT
1) WHEN AUTO OPERATING, RUNNING STATUS SIGNAL TURN OFF
2) WHEN START COMMAND SIGNAL ACTIVATING,
RUNNING STATUS SIGNAL WILL NOT ACTIVATE FOR FEW SECONDS
CAUSE & EFFECT DIAGRAM FOR
I-4101 POWDER TRANSFER PACKAGE 44C-40001A Protection
[8 empty] | PROJECT NAME | DRAWING NO | SHEET | REV
[8 empty] | PROJECT | 3944-VD-0171-DYP-RE-400-DIA-0082 | 8 | 0

## I-4201
I-4201 POWDER TRANSFER PACKAGE 44C-40001B Protection | [5 empty] | EFFECT | NOTES
ACTIVATED INTERLOCK NO.
[7 empty] | SERVICE DESCRIPTION | LEGEND :
P - PERMISSIVE
O - OPEN OR START
C - CLOSE
S - STOP OR SHUTDOWN
A - ACTIVE
OC - OPEN CLOSE
ALM : ALARM
SI : SIGNALING AND INDICATION
DT : DELAY TIME
R : RESET
D : DEACTIVATION
[7 empty] | TAG NO. EQ'T NO. | (a) : 44Z-40001A Selected (b) : 44Z-40001B Selected
[7 empty] | P&ID | NOTES :
CAUSE | [7 empty] | 1. ALL INSTRUMENT TAG NUMBERS SHALL BE PROVIDED WITH THE UNIT NUMBER (44) UNLESS INDICATED OTHER WISE
UNIT | P&ID | TAG NO. (TRIP INITIATOR) | SERVICE DESCRIPTION | INTERLOCK NO. | NOTES |  | ITEM | 2. POWDER TRANSFER PACKAGE IS CONTROLLED BY DCS
3. VALVE POSITION FAULT ALARM (DELAY TIME = 5 ~ 10 SECS)
4. RUN FAULT
1) WHEN AUTO OPERATING, RUNNING STATUS SIGNAL TURN OFF
2) WHEN START COMMAND SIGNAL ACTIVATING,
RUNNING STATUS SIGNAL WILL NOT ACTIVATE FOR FEW SECONDS
CAUSE & EFFECT DIAGRAM FOR
I-4201 POWDER TRANSFER PACKAGE 44C-40001B Protection
[8 empty] | PROJECT NAME | DRAWING NO | SHEET | REV
[8 empty] | PROJECT | 3944-VD-0171-DYP-RE-400-DIA-0082 | 8 | 0

## I-8001
I-8001 PELLET TRANSFER PACKAGE Pellet Handling System | [5 empty] | EFFECT | NOTES
ACTIVATED INTERLOCK NO.
[7 empty] | SERVICE DESCRIPTION | LEGEND :
P - PERMISSIVE
O - OPEN OR START
C - CLOSE
S - STOP OR SHUTDOWN
A - ACTIVE
OC - OPEN CLOSE
ALM : ALARM
SI : SIGNALING AND INDICATION
DT : DELAY TIME
R : RESET
D : DEACTIVATION
[7 empty] | TAG NO. EQ'T NO. | (a) : 44Z-40001A Selected (b) : 44Z-40001B Selected
[7 empty] | P&ID | NOTES :
CAUSE | [7 empty] | 1. ALL INSTRUMENT TAG NUMBERS SHALL BE PROVIDED WITH THE UNIT NUMBER (44) UNLESS INDICATED OTHER WISE
UNIT | P&ID | TAG NO. (TRIP INITIATOR) | SERVICE DESCRIPTION | INTERLOCK NO. | NOTES |  | ITEM | 2. POWDER TRANSFER PACKAGE IS CONTROLLED BY DCS
3. VALVE POSITION FAULT ALARM (DELAY TIME = 5 ~ 10 SECS)
4. RUN FAULT
1) WHEN AUTO OPERATING, RUNNING STATUS SIGNAL TURN OFF
2) WHEN START COMMAND SIGNAL ACTIVATING,
RUNNING STATUS SIGNAL WILL NOT ACTIVATE FOR FEW SECONDS
CAUSE & EFFECT DIAGRAM FOR
I-8001 PELLET TRANSFER PACKAGE Pellet Handling System
[8 empty] | PROJECT NAME | DRAWING NO | SHEET | REV
[8 empty] | PROJECT | 3944-VD-0171-DYP-RE-400-DIA-0082 | 8 | 0