## LEGEND-APPENDIX
INSTRUMENT INDEX LEGEND for LINE PROJECT
하기 내용은 AVEVA IMPLEMENTATION SPEC에 포함된 LEGEND로서 AVEVA 적용시 필수로 선택하여 적용 해야 함.
( LINE-000-ZA-4-0106 AVEVA Instrumentation Execution Procedure_Rev.0 )
INDEX 작업시 향후 AVEVA Import를 고려하여 최대한 균일하고 통일된 표현으로 작성한다
APPENDIX-01 | Instrument Type Catalogue | [5 empty] | APPENDIX-02 | Loop Type Catalogue |  | APPENDIX-04 | I/O Type | PLANT/UNIT Designation ( 1.1 Work Breakdown Structure (Plant Code / Unit Code) )
Class | Function | Description | I/O | Loc. | Wiring Rule | Remarks | Class | Loop Code | Description | I/O Type | Description | Plant | Unit |  |  | SCOPE
INS | AA | Analyzer Alarm |  | DCS |  |  | INSLoop | A | Analysis / Air Operated | - | No I/O |  | Code | Description | Short | WP1 | WP2 | WP3 | WP4 | WP5/7
INS | AAH | Analyzer Alarm High |  | DCS |  |  | INSLoop | B | Burner Flame / Beacon | AI | Analogue Input | 00 Common | 0 | General |  | O | O | O | O | O
INS | AAL | Analyzer Alarm Low |  | DCS |  |  | INSLoop | C | - | AIR | Analogue Input Redundant | 10 Ethylene | 0 | General |  | O | - | - | - | -
INS | AE | Chloride Analyzer Element(Sampling) |  | FLD |  |  | INSLoop | D | Deluge valve | AO | Analogue Output |  | 1 | Heater (Heater Section) |  | O | - | - | - | -
INS | AE | Chlorine Analyzer Element(Sampling) |  | FLD |  |  | INSLoop | E | Voltage (EMF) / Emergency | AOR | Analogue Output Redundant |  | 2 | Fractionator, Water Quench & Process Condensate (Quench Section) |  | O | - | - | - | -
INS | AE | CO2 Analyzer Element(Sampling) |  | FLD |  |  | INSLoop | F | Flow, Fire | DI | Digital Input |  | 3 | PGC, Acid Gas Removal, Gas Dryers, Depropanizer, Acetylene Reactor (Compressor Section) |  | O | - | - | - | -
INS | AE | COD Analyzer Element(Sampling) |  | FLD |  |  | INSLoop | G | Gas | DIR | Digital Input Redundant |  | 4 | Demethanizer, Cold Box, Expander (Separation Section) |  | O | - | - | - | -
INS | AE | Conductivity Analyzer Element(Sampling) |  | FLD |  |  | INSLoop | H | Hand Operated | DO | Digital Output |  | 5 | C2 Recovery, C2 Compressor, C2S |  | O | - | - | - | -
INS | AE | Density Analyzer Element(Sampling) |  | FLD |  |  | INSLoop | I | Electric Current | DOR | Digital Output Redundant |  | 6 | Debutanizer,C3 Recovery (MAPD, C3 Splitter) and C3 Refrigeration |  | O | - | - | - | -
INS | AE | Dew Point Analyzer Element(Sampling) |  | FLD |  |  | INSLoop | J | Power | PI | Pulse Input |  | 7 | GHT |  | O | - | - | - | -
INS | AE | DO Analyzer Element(Sampling) |  | FLD |  |  | INSLoop | K | Time & Time Schedule | PIR | Pulse Input Redundant | 20 Butadiene | 0 | General |  | - | - | O | - | -
INS | AE | Gas Chromatograph Element(Sampling) |  | FLD |  |  | INSLoop | L | Level / Leak | PO | Pulse Output |  | 1 | 1st Extractive Distillation |  | - | - | O | - | -
INS | AE | H2 Analyzer Element(Sampling) |  | FLD |  |  | INSLoop | M | Motor Operated | RTD | 3-Wire RTD Input |  | 2 | 2nd Extractive Distillation |  | - | - | O | - | -
INS | AE | H2O Analyzer Element(Sampling) |  | FLD |  |  | INSLoop | N | - | SAI | Serial Interface Analogue Input |  | 3 | Butadiene Purification |  | - | - | O | - | -
INS | AE | H2S/Sulphur Analyzer Element(Sampling) |  | FLD |  |  | INSLoop | O | - | SAO | Serial Interface Analogue Output |  | 4 | Solvent Purification |  | - | - | O | - | -
INS | AE | HC Analyzer Element(Sampling) |  | FLD |  |  | INSLoop | P | Pressure / Vacuum | SDI | Serial Interface Digital Input |  | 5 | Utilities |  | - | - | O | - | -
INS | AE | Moisture Analyzer Element(Sampling) |  | FLD |  |  | INSLoop | Q | Quantity / Event | SDO | Serial Interface Digital Output |  | 6 | Spare |  | - | - | O | - | -
INS | AE | OIL Analyzer Element(Sampling) |  | FLD |  |  | INSLoop | R | Radioactivity | SW | Software |  | 7 | Spare |  | - | - | O | - | -
INS | AE | OIW/TOC/COD Analyzer Element(Sampling) |  | FLD |  |  | INSLoop | S | Speed / Frequency | TC | Thermocouple Input |  | 8 | Spare |  | - | - | O | - | -
INS | AE | Oxygen Analyzer Element(Sampling) |  | FLD |  |  | INSLoop | T | Temperature |  |  |  | 9 | Cooling Tower #2 Package |  | - | - | O | - | -
INS | AE | pH Analyzer Element(Sampling) |  | FLD |  |  | INSLoop | U | Multivariable |  |  | 30 BTX / GHU | 0 | General / Battery Limit |  | - | - | O | - | -
INS | AE | pH/TOC Analyzer Element(Sampling) |  | FLD |  |  | INSLoop | V | Vibration | APPENDIX-05 | IS/NIS |  | 1 | GHU-I, DeC5, DeC8 |  | - | - | O | - | -
INS | AE | Silica Analyzer Element(Sampling) |  | FLD |  |  | INSLoop | W | Weight / Force | Signal Type | Description |  | 2 | GHU-II, H2S Stripper, Catalyst-regeneration Process |  | - | - | O | - | -
INS | AE | TOC Analyzer Element(Sampling) |  | FLD |  |  | INSLoop | X | On-Off | IS | Intrinsically Safe |  | 3 | Dec7, EDC, SRC |  | - | - | O | - | -
INS | AE | TSS Analyzer Element(Sampling) |  | FLD |  |  | INSLoop | Y | - | NIS | Non Intrinsically Safe |  | 4 | Clay, Tower, BZ Column, TOL Column |  | - | - | O | - | -
INS | AI | Analyzer Indicator |  | DCS |  |  | INSLoop | Z | Position / Displacement |  |  |  | 5 | Spare |  | - | - | O | - | -
INS | AIC | Indicating Controller |  | DCS | [8 empty] | 6 | Utility (Steam, N2, IA, PA, CW) |  | - | - | O | - | -
INS | AOV | Air Operated Valve - Ball |  | FLD | [8 empty] | 7 | Flare & Slop System |  | - | - | O | - | -
INS | AOV | Air Operated Valve - Butterfly |  | FLD |  |  | APPENDIX-03 | Process Units |  | APPENDIX-06 | System Type | 40 Spare | 0 | General |  | - | - | - | - | -
INS | AOV | Air Operated Valve - Gate |  | FLD |  |  | U Process Property | Units | Default | System Type | Description | 50 PP | 0 | General |  | - | O | - | - | -
INS | AT | Analyzer | AI | FLD | 2 Wire Tx To JB |  | Analyzer | %wt | O | APC | Advanced Process Control |  | 1 | Catalyst Preparation and Feeding |  | - | O | - | - | -
INS | AT | Chloride Analyzer | AI | FLD | 2 Wire Tx To JB |  |  | %vol |  | ASC | Anti-Surge Control System |  | 2 | Prepolymerization and Polymerization |  | - | O | - | - | -
INS | AT | Chlorine Analyzer | AI | FLD | 2 Wire Tx To JB |  |  | %mol |  | AUX | Auxiliary Panel or Console |  | 3 | Degassing and Monomer Recovery |  | - | O | - | - | -
INS | AT | CO2 Analyzer | AI | FLD | 2 Wire Tx To JB |  |  | ppm | O | BMS | Burner Management System |  | 4 | Copolymerization |  | - | O | - | - | -
INS | AT | COD Analyzer | AI | FLD | 2 Wire Tx To JB |  |  | kg/l | O | CC | Compressor Control Panel |  | 5 | Polymer Finishing |  | - | O | - | - | -
INS | AT | Conductivity Analyzer | AI | FLD | 2 Wire Tx To JB |  |  | kg/m³ |  | CCS | Compressor Control System |  | 6 | Blowdown and Process Facilities |  | - | O | - | - | -
INS | AT | Density Analyzer | AI | FLD | 2 Wire Tx To JB |  |  | lb/ft³ |  | CEMS | Continuous Emission Monitoring System |  | 7 | Monomer Treating |  | - | O | - | - | -
INS | AT | Dew Point Analyzer | AI | FLD | 2 Wire Tx To JB |  | Area | cm² |  | DCS | Distributed Control System |  | 8 | Pelletizing |  | - | O | - | - | -
INS | AT | DO Analyzer | AI | FLD | 2 Wire Tx To JB |  |  | ft² |  | ESD | Emergency Shutdown System |  | 9 | Pellet Storage |  | - | O | - | - | -
INS | AT | Gas Chromatograph | AI | FLD | 2 Wire Tx To JB |  |  | in² |  | FAP | Fire Alarm Panel | 55 Bagging & Automatic Warehouse | 0 | General & Common |  | - | O | - | - | -
INS | AT | H2 Analyzer | AI | FLD | 2 Wire Tx To JB |  |  | m² | O | FGS | Fire & Gas Detection System |  | 1 | Bagging System |  | - | O | - | - | -
INS | AT | H2O Analyzer | AI | FLD | 2 Wire Tx To JB |  |  | mm² |  | FMS | Flow Metering System |  | 2 | Automatic Warehouse |  | - | O | - | - | -
INS | AT | H2S/Sulphur Analyzer | AI | FLD | 2 Wire Tx To JB |  | Conductivity | µS/ cm | O | HIPPS | High Integrity Pressure Protection System | 60 : Spare | 0 | General |  | - | - | - | - | -
INS | AT | HC Analyzer | AI | FLD | 2 Wire Tx To JB |  | Current | A | O | HVAC | Heat, Ventilation and Air Conditioning system | 70 : Spare | 0 | General |  | - | - | - | - | -
INS | AT | Moisture Analyzer | AI | FLD | 2 Wire Tx To JB |  | Density | kg/l |  | ICSS | Instrument Control and Safety System ( DCS/ESD/FGS/RIE ) | 80 Utility | 0 | Common / General / Interconnection |  | - | - | - | O | -
INS | AT | OIL Analyzer | AI | FLD | 2 Wire Tx To JB |  |  | kg/m³ | O | LC | Local PLC/Microprocessor/Relay logic Panel |  | 1 | RWT & DW |  | - | - | - | O | -
INS | AT | OIW/TOC/COD Analyzer | AI | FLD | 2 Wire Tx To JB |  |  | lb/ft³ |  | MCC | Motor Control Center System |  | 2 | CPP/Demi/Deaerator |  | - | - | - | O | -
INS | AT | Oxygen Analyzer | AI | FLD | 2 Wire Tx To JB |  | Flow | in³/hr |  | MMS | Machine Monitoring System |  | 3 | Cooling Tower |  | - | - | - | O | -
INS | AT | pH Analyzer | AI | FLD | 2 Wire Tx To JB |  |  | in³/s |  | OTS | Operator Training System |  | 4 | Desalination |  | - | - | - | O | -
INS | AT | Silica Analyzer | AI | FLD | 2 Wire Tx To JB |  |  | kg/hr | O | PIMS | Plant Information Management System |  | 5 | WWT |  | - | - | - | O | -
INS | AT | TOC Analyzer | AI | FLD | 2 Wire Tx To JB |  |  | kg/s |  | PLC | Programmable Logic Controller |  | 6 | Fire Fighting |  | - | - | - | O | -
INS | AT | TSS Analyzer | AI | FLD | 2 Wire Tx To JB |  |  | lb/hr |  | TGS | Tank Gauging System |  | 7 | Air / N2 |  | - | - | - | O | -
INS | AX | Soft Function |  | DCS |  |  |  | lb/min |  | TCS | Turbine Control System |  | 8 | Flare |  | - | - | - | O | -
INS | AZIC | Position Indicator - Close |  | DCS |  | Alter |  | m³/hr |  | TLS | Truck Loading System |  | 9 | Spare |  | - | - | - | O | -
INS | AZIO | Position Indicator - Open |  | DCS |  | Alter |  | m³/min |  | UC | Unit Control Panel ( PLC system supplied by Package Vendor ) | 89 LCTN | 0 | Common / General |  | - | - | - | O | -
INS | AZLC | Position Indicator - Close |  | DCS |  | Preferred |  | Nm³/hr |  | UCP | Unit Control Panel ( PLC system supplied by Package Vendor ) | 90 OS & Jetty | 0 | Common / General |  | - | - | - | - | O
INS | AZLO | Position Indicator - Open |  | DCS |  | Preferred |  | t/d |  |  |  |  | 1 | Tankage (Naphtha) |  | - | - | - | - | O
INS | AZSC | Valve Close Limit Switch | DI | FLD | 2 Wire Switch (NO) To JB |  |  | t/hr |  |  |  |  | 2 | Tankage (EL/PL/C3/C4) |  | - | - | - | - | O
INS | AZSO | Valve Open Limit Switch | DI | FLD | 2 Wire Switch (NO) To JB |  |  | US gal/d |  | APPENDIX-07 | Location or SYSTEM Location |  | 3 | Tankage (Sphere) |  | - | - | - | - | O
INS | BA | Burner Switch Alarm |  | DCS |  |  |  | US gal/min |  | Location | Description |  | 4 | Tankage (Others) |  | - | - | - | - | O
INS | BAH | Burner Flame Intensity High |  | DCS |  |  |  | US gal/s |  | AC | Analyzer Cabinet |  | 5 | Sea Water |  | - | - | - | - | O
INS | BAL | Burner Flame Intensity Low |  | DCS |  |  | Frequency | Hz | O | AR | Analyzer Rack |  | 6 | Jetty |  | - | - | - | - | O
INS | BE | Flame Scanner for Burner | DI | FLD | 2 Wire Switch (NO) To JB |  |  | kHz |  | AS | Analyzer Shelter |  | 7 | Spare |  | - | - | - | - | O
INS | BI | Burner Indicator |  | DCS |  |  |  | rpm |  | AUX-E | ESD Auxiliary Console
INS | BS | Burner Flame Detector Switch | DI | FLD | 2 Wire Switch (NO) To JB |  | Length | cm |  | AUX-F | FGS Auxiliary Console
INS | BS | Burner Switch | DI | FLD | 2 Wire Switch (NO) To JB |  |  | in |  | CC | Compressor Control Panel
INS | BS | Heat Detector | DI | FLD | 2 Wire Switch (NO) To JB |  |  | km |  | FLD | Field
INS | BT | Burner Flame Detector | AI | FLD |  |  |  | m |  | FS | Fire Station
INS | BV | Pressure / Vacuum Relief Valve |  | FLD |  |  |  | mm | O | IRP | Interposing Relay Panel
INS | BV | Vacuum Relief Valve |  | FLD |  |  | Level | cm |  | LC | Local PLC/Microprocessor/Relay logic Panel
INS | DI | Density Indicator |  | FLD |  |  |  | in |  | LCB | Local Control Building
INS | DS | Desuperheater |  | FLD |  | Preferred |  | mm | O | LCP | Local Control Panel
INS | DV | Deluge Valve |  | FLD |  |  | Mass | kg | O | LCR | Local Control Room
INS | DY | Solenoid Valve | DO | FLD |  |  |  | lb |  | LGB | Local Gauge Board
INS | DZ | Remote Operation Signal For DV |  | FGS |  |  |  | oz |  | LH | Local HMI
INS | DZLC | Position Indicator - Close |  | DCS |  |  | Pressure | bar | O | LMCB | LCTN Main Control Building
INS | DZLO | Position Indicator - Open |  | DCS |  |  |  | bar-a |  | LOP | Local Operation Panel
INS | DZSC | Valve Close Limit Switch | DI | FLD | 2 Wire Switch (NO) To JB |  |  | bar-g |  | LP | Local Operation Panel
INS | DZSO | Valve Open Limit Switch | DI | FLD | 2 Wire Switch (NO) To JB |  |  | in H2O |  | LW | Local Workstation
INS | ESD | Shutdown | DO | ESD | 2 Wire Switch (NO) To JB |  |  | kg/cm² | O | MCB | Main Control Building
INS | EVC | Emergency Vent Cover |  | FLD |  |  |  | kg/cm²-a |  | MCC | Motor Control Center
INS | EWH | Motor High Speed |  | DCS |  |  |  | kg/cm²-g | O | MCR | Main Control Room ( in MCB )
INS | EWL | Motor Low Speed |  | DCS |  |  |  | kg/m² |  | MER | Main Engineering Room ( in MCB )
INS | FA | Flame Arrestor |  | FLD |  |  |  | kPa |  | MP | Marshalling Panel
INS | FAH | Flow Alarm High |  | DCS |  |  |  | kPa-a |  | MRR | Main Rack Room ( in MCB )
INS | FAHH | Flow Alarm High High |  | DCS |  |  |  | kPa-g |  | OTR | Operator Training Simulation Room
INS | FAL | Flow Alarm Low |  | DCS |  |  |  | lb/in² |  | RIO | Remote I/O Panel
INS | FALL | Flow Alarm Low Low |  | DCS |  |  |  | lbf/ft² |  | SS | Substation
INS | FD | Flame Detector | DI | FLD |  |  |  | mbar |  | UC | Unit Control Panel
INS | FDA | Flame Detection Alarm |  | DCS |  |  |  | mm H2O |  | UOP | Unit Operation Panel in RIE or Local Control Room
INS | FDI | Flame Detector Indication |  | DCS |  |  |  | mm H2O-a
INS | FDT | Flame Detector | AI | FLD | 2 Wire Switch (NO) To JB |  |  | mm H2O-g |  | 10-RIE-001 | Remote Instrument Enclosure (Furnace)
INS | FE | Averaging Pitot Tube Element |  | FLD |  |  |  | MPa |  | 10-RIE-002 | Remote Instrument Enclosure (NCC Comp.)
INS | FE | Orifice Assembly |  | FLD |  |  |  | Pa |  | 10-RIE-003 | Remote Instrument Enclosure (NCC Cold)
INS | FE | Orifice Plate - Radius Tap |  | FLD |  |  |  | Pa-a |  | 10-RIE-004 | Remote Instrument Enclosure (NCC Utility & QUNCH )
INS | FE | Parshall Flume Element |  | FLD |  |  |  | Pa-g |  | 20-RIE-001 | Remote Instrument Enclosure (BD)
INS | FE | Venturi Tube Flow Element |  | FLD |  |  |  | psi |  | 30-RIE-001 | Remote Instrument Enclosure (BTX)
INS | FE | Wedge Flowmeter |  | FLD |  |  |  | psi-a |  | 50-RIE-001 | Remote Instrument Enclosure (PP)
INS | FFAL | Ratio Alarm Low |  | DCS |  |  |  | psi-g |  | 80-RIE-001 | Remote Instrument Enclosure (UTILITY)
INS | FFIC | Indicating Controller (Flow Ratio) |  | DCS |  |  | Temperature | ºC | O | 81-RIB-001 | Remote Instrument Building (RWT)
INS | FG | DP Flow Gauge |  | FLD |  |  |  | ºF |  | 85-RIB-001 | Remote Instrument Building (WWT)
INS | FG | Variable Area Flowmeter |  | FLD |  | Preferred |  | K |  | 90-RIE-001 | Remote Instrument Enclosure (TANKAGE)
INS | FGAH | Gas Alarm High |  | FGS |  |  | Vibration | mm/s² RMS | O
INS | FGAHH | Gas Alarm High High |  | FGS |  |  |  | m/s² RMS |  | 10-SS-001 | Substation for NCC
INS | FGD | Flammable Gas Detector (IR type) | AI | FLD |  |  |  | mm/s RMS | O | 30-SS-001 | Substation for BD/BTX
INS | FGD | H2 Detector (Catalytic type) | AI | FLD |  |  |  | mm | O | 50-SS-001 | Substation for PP
INS | FGI | Gas Indicator |  | FGS |  |  |  | RPM | O | 80-SS-101 | RWT Substation
INS | FI | Flow Indicator |  | DCS |  |  | Viscosity | cP | O | 80-SS-202 | UT-1 Substation
INS | FI | Flow Indicator - Local |  | FLD | Series connection | FI-****A |  | mPa.s |  | 80-SS-303 | UT-2 Substation
INS | FI | Variable Area Flowmeter |  | FLD |  | Alter | Weight | g |  | 90-SS-001 | Substation for Tank
INS | FIC | Indicating Controller |  | DCS |  |  |  | kg | O
INS | FO | Restriction Orifice |  | FLD |  | Preferred |  | t |  | 10-B-101 | Elevator for Furnace
INS | FPY | I/P Converter | AO | FLD | I/P To JB |  |  |  |  | 10-B-001 | Operator Shelter-1
INS | FQI | Local Totalized Flow Indicator |  | FLD | [5 empty] | 10-B-002 | Operator Shelter-2
INS | FQI | Totalized Flow Indicator |  | DCS | [5 empty] | 20-B-001 | Compressor shelter for BD
INS | FQIC | Local Flow Totalizer Controller |  | FLD | [5 empty] | 30-B-005 | Operator Building for BTX, BD
INS | FSH | Flow Switch High | DI | FLD | 2 Wire Switch (NO) To JB |  |  |  |  | 50-B-002 | Extrusion building
INS | FSL | Flow Switch Low | DI | FLD | 2 Wire Switch (NO) To JB |  |  |  |  | 50-B-007 | Truck Scale Control Shelter
INS | FT | Coriolis Flow Transmitter | AI | FLD | 2 Wire Tx To JB |  |  |  |  | 50-B-013 | Auto Warehouse & Bagging house
INS | FT | DP Flow Transmitter | AI | FLD | 2 Wire Tx To JB |  |  |  |  | 80-B-205 | Condensate Polishing Shelter
INS | FT | DP Flow Transmitter - Diaphragm Seal | AI | FLD | 2 Wire Tx To JB |  |  |  |  | 80-B-210 | Main Control Building
INS | FT | Integral Orifice DP Flow Transmitter | AI | FLD | 2 Wire Tx To JB |  |  |  |  | 80-B-906 | Fire Station & HSE Building
INS | FT | Magnetic Flow Transmitter | AI | FLD | 2 Wire Tx To JB |  |  |  |  | 90-B-012 | Jetty Control Building
INS | FT | Parshall Flume Flow Transmitter | AI | FLD | 2 Wire Tx To JB
INS | FT | Pitot Tube Flow Transmitter | AI | FLD | 2 Wire Tx To JB |  |  |  |  | 10-AS-001 | Analyzer shelter for NCC
INS | FT | Thermal/Mass Flow Meter |  | FLD | [5 empty] | 10-AS-003 | Analyzer shelter for NCC
INS | FT | Turbine Flowmeter |  | FLD | [5 empty] | 10-AS-004 | Analyzer shelter for NCC
INS | FT | Ultrasonic Flow Transmitter | AI | FLD | 2 Wire Tx To JB |  |  |  |  | 10-AS-005 | Analyzer shelter for NCC
INS | FT | Vortex Flow Transmitter | AI | FLD | 2 Wire Tx To JB |  |  |  |  | 10-AS-006 | Analyzer shelter for NCC
INS | FV | Control Valve - Angle |  | FLD | [5 empty] | 50-AS-001 | Analyzer shelter for PP
INS | FV | Control Valve - Butterfly |  | FLD | [5 empty] | 20-AS-001 | Analyzer shelter for BD
INS | FV | Control Valve - Globe |  | FLD | [5 empty] | 30-AS-001 | Analyzer shelter for BTX
INS | FV | Control Valve - V-Ball |  | FLD
INS | FX | Soft Function |  | DCS
INS | FY | Solenoid Valve | DO | FLD
INS | FY | Stroke Control | AO | FLD | [5 empty] | APPENDIX-08 | Scope
INS | FZI | Valve Position Indicator |  | DCS | [5 empty] | Status | Description
INS | FZIC | Position Indicator - Close |  | DCS |  | Alter |  |  |  | NEW | New Instrument
INS | FZIO | Position Indicator - Open |  | DCS |  | Alter |  |  |  | EXIST | Existing Instrument (LCTN or Other )
INS | FZLC | Position Indicator - Close |  | DCS |  | Preferred |  |  |  | DEL | Deleted
INS | FZLO | Position Indicator - Open |  | DCS |  | Preferred |  |  |  | OTHER | Supplied by Others
INS | FZSC | Valve Close Limit Switch | DI | FLD | 2 Wire Switch (NO) To JB |  |  |  |  | PKG | Supplied by Package Vendor
INS | FZSO | Valve Open Limit Switch | DI | FLD | 2 Wire Switch (NO) To JB |  |  |  |  | SPARE | Spare Instrument
INS | FZT | Valve Position Transmitter | AI | FLD | 2 Wire Tx To JB |  |  |  |  | FUTURE | Instrument for Future purpose
INS | GA | Beacon | DO | FLD | [5 empty] | EPC | Supplied by EPC Contractor (Instrument)
INS | GA | Sounder | DO | FLD | [5 empty] | EPC: RFQ Plan에 따른 HEC/LEC 제어가 구매하는 계기 (대응되는 PO no.가 해당 열에 기재되어야 함)
INS | GAH | Gas Alarm High |  | FGS
INS | GAHH | Gas Alarm High High |  | FGS
INS | GAS | Gas Alarm Sounder |  | FLD | [5 empty] | APPENDIX-09 | Accessory
INS | GFAS | Gas And Fire Alarm Sounder (2 Stage) |  | FLD | [5 empty] | Accessory | Description
INS | GI | Gas Indicator |  | FGS | [5 empty] | 3SV | 3-Way Solenoid Valve
INS | GT | Flammable Gas Detector (IR type) | AI | FLD | [5 empty] | 3SV x 2 | 3-Way Solenoid Valve x 2
INS | GT | H2 Detector (Catalytic type) | AI | FLD
INS | GT | Toxic Gas Detector | AI | FLD | [5 empty] | 4SV | 4-Way Solenoid Valve
INS | GVA | Gas Visual Alarm Beacon/Strobe |  | FLD | [5 empty] | AFR | Air Filter Regulator
INS | HIC | Hand Controller |  | DCS
INS | HL | Auto/Manual Selection |  | DCS | [5 empty] | DP | Dampener
INS | HL | Permissive ( for To Re-Open or Close. Etc) |  | DCS | [5 empty] | FLT | Filter
INS | HPY | I/P Converter | AO | FLD | I/P To JB
INS | HS | Duty Select |  | DCS | [5 empty] | GP | Gauge Protector
INS | HS | Hand Switch | DI | FLD | 2 Wire Switch (NO) To JB |  |  |  |  | GV | Gauge Valve for Pressure Gauge
INS | HS | Hand Switch - Remote |  | DCS | [5 empty] | HW | Hand Wheel
INS | HS | Hand Switch (Local Control) | DI | FLD | 2 Wire Switch (NO) To JB |  |  |  |  | IP | I/P Positioner
INS | HS | Local Isolator |  | FLD | [5 empty] | LV | Lock-Up Valve
INS | HS | Local Start Switch | DI | FLD | 2 Wire Switch (NO) To JB |  |  |  |  | PST | PST Device
INS | HS | Manual Field Reset Switch | DI | FLD | 2 Wire Switch (NO) To JB |  |  |  |  | SK | Safety Kloser (for PG)
INS | HS | Motor Emergency Stop Command | DI | FLD | 2 Wire Switch (NO) To JB |  |  |  |  | SP | Surge Protector
INS | HS | Motor Run Switch | DO | FLD | 2 Wire Switch (NO) To JB |  |  |  |  | ST | Syphon Tube
INS | HS | Motor Start/Stop Hand Switch | DI | FLD | 2 Wire Switch (NO) To JB |  |  |  |  | VT | Volume Tank
INS | HS | Motor Start/Stop Hand/Off/Auto | DI | FLD | 2 Wire Switch (NO) To JB |  |  |  |  | ZSC/ZSO | Limit Switch (ZSC : Close, ZSO : Open)
INS | XSS | Motor Stop Command | DO | FLD | 2 Wire Switch (NO) To JB |  |  |  |  | Accessory 표현은 권장사항임. 추가 사항은 INDEX상 자유 표기
INS | XSS | Motor Stop Command | DO | DCS |  | To ESD
INS | XSS | Motor Stop Command | DI | ESD |  | From DCS
INS | HV | Control Valve - Angle |  | FLD
INS | HV | Control Valve - Butterfly |  | FLD
INS | HV | Control Valve - Globe |  | FLD
INS | HV | Control Valve - V-Ball |  | FLD
INS | HV | Diverter Valve |  | FLD
INS | HV | On/off Control Valve - 3-way Ball |  | FLD
INS | HV | On/off Control Valve - Ball |  | FLD
INS | HV | On/off Control Valve - Butterfly |  | FLD
INS | HV | On/off Control Valve - Gate |  | FLD
INS | HV | On/off Control Valve - Plug |  | FLD
INS | HV | On/off Control Valve - Ram Piston |  | FLD
INS | HV | On/off Control Valve - Slide Gate |  | FLD
INS | HY | Solenoid Valve | DO | FLD
INS | HZIC | Position Indicator - Close |  | DCS |  | Alter
INS | HZIO | Position Indicator - Open |  | DCS |  | Alter
INS | HZLA | Position Indicator - Through |  | DCS
INS | HZLB | Position Indicator - Divert |  | DCS
INS | HZLC | Position Indicator - Close |  | DCS |  | Preferred
INS | HZLO | Position Indicator - Open |  | DCS |  | Preferred
INS | HZSA | Valve Through Position Limit Switch | DI | FLD | 2 Wire Switch (NO) To JB
INS | HZSB | Valve Divert Position Limit Switch | DI | FLD | 2 Wire Switch (NO) To JB
INS | HZSC | Valve Close Limit Switch | DI | FLD | 2 Wire Switch (NO) To JB
INS | HZSO | Valve Open Limit Switch | DI | FLD | 2 Wire Switch (NO) To JB
INS | IAH | Ammeter Alarm High |  | DCS
INS | II | Ammeter Indicator |  | DCS
INS | IT | Ammeter Transmitter | AI | FLD
INS | KE | Key Phasor Sensor |  | FLD
INS | KI | Key Phasor Indicator |  | DCS
INS | KT | Key Phasor Transmitter | AI | FLD
INS | LA | Leak Detecting Alarm |  | FGS
INS | LAH | Level Alarm High |  | DCS
INS | LAHH | Level Alarm High High |  | DCS
INS | LAHHH | Level Alarm High High High |  | DCS
INS | LAL | Level Alarm Low |  | DCS
INS | LALL | Level Alarm Low Low |  | DCS
INS | LD | Leak Detector | DI | FLD
INS | LG | Level Gauge - Float |  | FLD
INS | LG | Level Gauge - Large Chamber |  | FLD
INS | LG | Level Gauge - Magnetic |  | FLD
INS | LG | Level Gauge - Reflex |  | FLD
INS | LG | Level Gauge - Transparent |  | FLD
INS | LI | Level Indicator |  | DCS
INS | LI | Level Indicator - Local |  | FLD | Series connection | LI-****A
INS | LIC | Indicating Controller |  | DCS
INS | LPY | I/P Converter | AO | FLD | I/P To JB
INS | LSH | Level Switch High | DI | FLD | 2 Wire Switch (NO) To JB
INS | LSH | Level Switch(Vibration Pork) High | DI | FLD | 2 Wire Switch (NO) To JB
INS | LSHH | Level Switch High High | DI | FLD | 2 Wire Switch (NO) To JB
INS | LSL | Level Switch Low | DI | FLD | 2 Wire Switch (NO) To JB
INS | LSLL | Level Switch Low Low | DI | FLD | 2 Wire Switch (NO) To JB
INS | LT | DP Level Transmitter - Diaph Seal (Direct) | AI | FLD | 2 Wire Tx To JB
INS | LT | DP Level Transmitter | AI | FLD | 2 Wire Tx To JB
INS | LT | DP Level Transmitter - Diaphragm Seal | AI | FLD | 2 Wire Tx To JB
INS | LT | GWR Level Transmitter | AI | FLD | 2 Wire Tx To JB
INS | LT | Level Transmitter - Displacer Type | AI | FLD | 2 Wire Tx To JB
INS | LT | Radar Level Transmitter | AI | FLD | 2 Wire Tx To JB
INS | LTD | Level/Temperature/Density Gauge |  | FLD
INS | LV | Control Valve - Angle |  | FLD
INS | LV | Control Valve - Butterfly |  | FLD
INS | LV | Control Valve - Globe |  | FLD
INS | LV | Control Valve - V-Ball |  | FLD
INS | LX | Soft Function |  | DCS
INS | LY | Auto Start/Stop | AO | FLD
INS | LY | Solenoid Valve | DO | FLD
INS | LZI | Valve Position Indicator |  | DCS
INS | LZIC | Position Indicator - Close |  | DCS |  | Alter
INS | LZIO | Position Indicator - Open |  | DCS |  | Alter
INS | LZLC | Position Indicator - Close |  | DCS |  | Preferred
INS | LZLO | Position Indicator - Open |  | DCS |  | Preferred
INS | LZSC | Valve Close Limit Switch | DI | FLD | 2 Wire Switch (NO) To JB
INS | LZSO | Valve Open Limit Switch | DI | FLD | 2 Wire Switch (NO) To JB
INS | LZT | Valve Position Transmitter | AI | FLD | 2 Wire Tx To JB
INS | ME | Desuperheater |  | FLD |  | Alter
INS | MHS | LCS/DCS Select Switch | DI | LCS
INS | MHSC | MOV Close Command | DO | FLD | 2 Wire Tx To JB
INS | MHSC | MOV Close Command Local |  | FLD |  | MHSC-****A
INS | MHSO | MOV Open Command | DO | FLD | 2 Wire Tx To JB
INS | MHSO | MOV Open Command Local |  | FLD |  | MHSO-****A
INS | MHSS | MOV Stop Command | DO | FLD | 2 Wire Tx To JB
INS | MOV | Motor Operated Valve - Ball |  | FLD
INS | MOV | Motor Operated Valve - Butterfly |  | FLD
INS | MOV | Motor Operated Valve - Gate |  | FLD
INS | MZIC | Position Indicator - Close |  | DCS |  | Alter
INS | MZIO | Position Indicator - Open |  | DCS |  | Alter
INS | MZLC | Position Indicator - Close |  | DCS |  | Preferred
INS | MZLO | Position Indicator - Open |  | DCS |  | Preferred
INS | MZSC | Valve Close Limit Switch | DI | FLD | 2 Wire Tx To JB
INS | MZSO | Valve Open Limit Switch | DI | FLD | 2 Wire Tx To JB
INS | MZXA | Valve Common Fault | DI | FLD | 2 Wire Tx To JB
INS | PAH | Pressure Alarm High |  | DCS
INS | PAHH | Pressure Alarm High High |  | DCS
INS | PAL | Pressure Alarm Low |  | DCS
INS | PALL | Pressure Alarm Low Low |  | DCS
INS | PB | Push Button |  | FLD
INS | PBL | Push Button(s) with Light(s) |  | FLD
INS | PCV | Pressure Regulating Valve |  | FLD
INS | PCV | Pressure Regulator - Downstream Sensing |  | FLD
INS | PCV | Pressure Regulator - Pilot |  | FLD
INS | PDA | Pressure Alarm |  | DCS
INS | PDAH | Diff Pressure Alarm High |  | DCS
INS | PDAHH | Diff Pressure Alarm High High |  | DCS
INS | PDAL | Diff Pressure Alarm Low |  | DCS
INS | PDALL | Diff Pressure Alarm Low Low |  | DCS
INS | PDCV | DP Reducing Regulator |  | DCS
INS | PDG | Diff Pressure Gauge |  | FLD
INS | PDI | Diff Pressure Indicator |  | DCS
INS | PDI | Diff Pressure Indicator - Local |  | FLD | Series connection | PDI-****A
INS | PDIC | Indicating Controller |  | DCS
INS | PDSH | Diff Pressure Switch | DI | FLD | 2 Wire Switch (NO) To JB
INS | PDT | Diff Pressure Transmitter | AI | FLD | 2 Wire Tx To JB
INS | PDT | Diff Pressure Transmitter - Diaphragm Seal | AI | FLD | 2 Wire Tx To JB
INS | PDX | Soft Function |  | DCS
INS | PG | Pressure Gauge(Bellows) |  | FLD
INS | PG | Pressure Gauge(Bourdon) |  | FLD
INS | PG | Pressure Gauge(Diaphragm) |  | FLD
INS | PG | Vacuum Gauge |  | FLD
INS | PI | Pressure Indicator |  | DCS
INS | PI | Pressure Indicator - Local |  | FLD | Series connection | PI-****A
INS | PIC | Indicating Controller |  | DCS
INS | PIC | Local Controller |  | FLD
INS | PPY | I/P Converter | AO | FLD | I/P To JB
INS | PSE | Rupture Disc |  | FLD |  | Preferred
INS | PSH | Pressure Switch High | DI | FLD | 2 Wire Switch (NO) To JB
INS | PSHH | Pressure Switch High High | DI | FLD | 2 Wire Switch (NO) To JB
INS | PSL | Pressure Switch Low | DI | FLD | 2 Wire Switch (NO) To JB
INS | PSLL | Pressure Switch Low Low | DI | FLD | 2 Wire Switch (NO) To JB
INS | PSV | Safety Relief Valve |  | FLD
INS | PSV | Thermal Relief valve |  | FLD |  | Alter
INS | PT | Pressure Transmitter | AI | FLD | 2 Wire Tx To JB
INS | PT | Pressure Transmitter - Diaphragm Seal | AI | FLD | 2 Wire Tx To JB
INS | PV | Control Valve - Angle |  | FLD
INS | PV | Control Valve - Butterfly |  | FLD
INS | PV | Control Valve - Globe |  | FLD
INS | PV | Control Valve - V-Ball |  | FLD
INS | PVRV | Breather Valve |  | FLD
INS | PVRV | Pressure/ Vacuum Relief Valve |  | FLD
INS | PX | Soft Function |  | DCS
INS | PY | Solenoid Valve | DO | FLD
INS | PZI | Valve Position Indicator |  | DCS
INS | PZIC | Position Indicator - Close |  | DCS |  | Alter
INS | PZIO | Position Indicator - Open |  | DCS |  | Alter
INS | PZLC | Position Indicator - Close |  | DCS |  | Preferred
INS | PZLO | Position Indicator - Open |  | DCS |  | Preferred
INS | PZSC | Valve Close Limit Switch | DI | FLD | 2 Wire Switch (NO) To JB
INS | PZSO | Valve Open Limit Switch | DI | FLD | 2 Wire Switch (NO) To JB
INS | PZT | Valve Position Transmitter | AI | FLD | 2 Wire Tx To JB
INS | RD | Rupture Disc |  | FLD |  | Alter
INS | RO | Restriction Orifice |  | FLD |  | Alter
INS | SAH | Speed Alarm High |  | DCS
INS | SAHH | Speed Alarm High High |  | DCS
INS | SC | Sample Connection |  | FLD
INS | SG | Sight Glass |  | FLD
INS | SI | Speed Indicator |  | DCS
INS | SIC | Speed Controller |  | DCS
INS | ST | Speed Transmitter | AI | FLD | 2 Wire Tx To JB
INS | SY | VSD Control | AO | FLD | 2 Wire Tx To JB
INS | TAH | Local Alarm | AO | FLD
INS | TAH | Temperature Alarm High |  | DCS
INS | TAHH | Temperature Alarm High High |  | DCS
INS | TAL | Temperature Alarm Low |  | DCS
INS | TALL | Temperature Alarm Low Low |  | DCS
INS | TE | RTD Temperature Element |  | FLD
INS | TE | RTD Temperature Element (direct) | RTD | FLD | RTD To JB
INS | TE | Skin Type RTD Temperature Element | RTD | FLD
INS | TE | Skin Type Thermocouple Element - Type J | T/C | FLD
INS | TE | Skin Type Thermocouple Element - Type K | T/C | FLD
INS | TE | Thermocouple Element - Type J |  | FLD
INS | TE | Thermocouple Element - Type J (direct) | T/C | FLD | T/C (type J) To JB
INS | TE | Thermocouple Element - Type K |  | FLD
INS | TE | Thermocouple Element - Type K (direct) | T/C | FLD | T/C (type K) To JB
INS | TE/TT | RTD with Transmitter | AI | FLD
INS | TE/TT | T/C Type J with Transmitter | AI | FLD
INS | TE/TT | T/C Type K with Transmitter | AI | FLD
INS | TG | Temperature Gauge |  | FLD
INS | TG | Temperature Gauge (Capillary) |  | FLD
INS | TGAH | Gas Alarm High |  | FGS
INS | TGAHH | Gas Alarm High High |  | FGS
INS | TGD | Toxic Gas Detector | AI | FLD
INS | TGI | Gas Indicator |  | FGS
INS | TI | Temperature Indicator |  | DCS
INS | TI | Temperature Indicator - Local |  | FLD | Series connection | TI-****A
INS | TIC | Indicating Controller |  | DCS
INS | TIC | Local Controller |  | FLD
INS | TPY | I/P Converter | AO | FLD | I/P To JB
INS | TSH | Temperature Switch High | DI | FLD | 2 Wire Switch (NO) To JB
INS | TSHH | Temperature Switch High High | DI | FLD | 2 Wire Switch (NO) To JB
INS | TSL | Temperature Switch Low | DI | FLD | 2 Wire Switch (NO) To JB
INS | TSLL | Temperature Switch Low Low |  | FLD | 2 Wire Switch (NO) To JB
INS | TSV | Thermal Relief valve |  | FLD |  | Preferred
INS | TT | Temperature Transmitter | AI | FLD | 2 Wire Tx To JB
INS | TV | Control Valve - Angle |  | FLD
INS | TV | Control Valve - Butterfly |  | FLD
INS | TV | Control Valve - Globe |  | FLD
INS | TV | Control Valve - V-Ball |  | FLD
INS | TW | Thermowell |  | FLD
INS | TX | Soft Function |  | DCS
INS | TY | Solenoid Valve | DO | FLD
INS | TZI | Valve Position Indicator |  | DCS
INS | TZIC | Position Indicator - Close |  | DCS |  | Alter
INS | TZIO | Position Indicator - Open |  | DCS |  | Alter
INS | TZLC | Position Indicator - Close |  | DCS |  | Preferred
INS | TZLO | Position Indicator - Open |  | DCS |  | Preferred
INS | TZSC | Valve Close Limit Switch | DI | FLD | 2 Wire Switch (NO) To JB
INS | TZSO | Valve Open Limit Switch | DI | FLD | 2 Wire Switch (NO) To JB
INS | TZT | Valve Position Transmitter | AI | FLD | 2 Wire Tx To JB
INS | UA | Alarm |  | DCS
INS | UC | Duty Controller |  | DCS
INS | VAH | Vibration Alarm High |  | DCS
INS | VAH | Vibration Alarm High - X |  | DCS |  | VAH-****X
INS | VAH | Vibration Alarm High - Y |  | DCS |  | VAH-****Y
INS | VAH | Vibration Alarm High - Z |  | DCS
INS | VAHH | Vibration Alarm High High |  | DCS
INS | VAHH | Vibration Alarm High High - X |  | DCS |  | VAHH-****X
INS | VAHH | Vibration Alarm High High - Y |  | DCS |  | VAHH-****Y
INS | VAHH | Vibration Alarm High High - Z |  | DCS
INS | VE | Accelerometer |  | FLD | 2 Wire Tx To JB
INS | VE | Proximity Vibration Sensor - X |  | FLD |  | VE-****X
INS | VE | Proximity Vibration Sensor - Y |  | FLD |  | VE-****Y
INS | VE | Proximity Vibration Sensor - Z |  | FLD
INS | VE | Velometer |  | FLD | 2 Wire Tx To JB
INS | VI | Accelerometer Indicator |  | DCS
INS | VI | Velometer Indicator |  | DCS
INS | VI | Vibration Indicating - X |  | DCS |  | VI-****X
INS | VI | Vibration Indicating - Y |  | DCS |  | VI-****Y
INS | VI | Vibration Indicating - Z |  | DCS
INS | VI | Vibration Indicator |  | DCS
INS | VRV | Vacuum Relief Valve |  | FLD
INS | VSH | Vibration Switch | DI | FLD | 2 Wire Switch (NO) To JB
INS | VSHH | Vibration Switch | DI | FLD | 2 Wire Switch (NO) To JB
INS | VT | Accelerometer Transmitter | AI | FLD | 2 Wire Tx To JB
INS | VT | Proximity Vibration Transmitter - X | AI | FLD |  | VT-****X
INS | VT | Proximity Vibration Transmitter - Y | AI | FLD |  | VT-****Y
INS | VT | Proximity Vibration Transmitter - Z | AI | FLD
INS | VT | Velometer Transmitter | AI | FLD | 2 Wire Tx To JB
INS | VT | Vibration Transmitter | AI | FLD
INS | VYS | Vibration Relay Output | DO | DCS
INS | WI | Weight Indicator |  | DCS
INS | WT | Weight Transmitter | AI | FLD | 2 Wire Tx To JB
INS | XA | Common Alarm |  | DCS
INS | XA | Motor Fault | DI | DCS
INS | XA | Turbine Shutdown Fault |  | DCS
INS | XAM | Alarm |  | DCS
INS | XHS | On-off Valve Hand Switch - Remote | DO | DCS |  | To ESD
INS | XHS | On-off Valve Hand Switch - Remote | DI | ESD |  | From DCS
INS | XHS | On-off Valve Hand Switch - Remote | DO | ESD
INS | XI | Motor Auto Status |  | DCS
INS | XI | Motor Local/Remote Status | DI | DCS
INS | XL | Motor Status |  | DCS
INS | XPY | Partial Stroke Positioner | AO | DCS
INS | XS | Local Switch | DI | FLD | 2 Wire Switch (NO) To JB
INS | XS | Switch for Interface between System | DI | DCS | 2 Wire Switch (NO) To JB
INS | XS | Switch for Interface between System | DO | DCS | 2 Wire Switch (NO) To JB
INS | XSS | Motor Trip(Stop) Command | DO | DCS
INS | XST | Motor Start Command | DO | DCS
INS | XV | On/off Valve - 3-way Ball |  | FLD
INS | XV | On/off Valve - Ball |  | FLD
INS | XV | On/off Valve - Butterfly |  | FLD
INS | XV | On/off Valve - Gate |  | FLD
INS | XV | On/off Valve - Plug |  | FLD
INS | XV | On/off Valve - Ram Piston |  | FLD
INS | XV | On/off Valve - Slide Gate |  | FLD
INS | XY | Solenoid Valve | DO | FLD
INS | XZIC | Position Indicator - Close |  | DCS |  | Alter
INS | XZIO | Position Indicator - Open |  | DCS |  | Alter
INS | XZLC | Position Indicator - Close |  | DCS |  | Preferred
INS | XZLO | Position Indicator - Open |  | DCS |  | Preferred
INS | XZSC | Valve Close Limit Switch | DI | FLD | 2 Wire Switch (NO) To JB
INS | XZSO | Valve Open Limit Switch | DI | FLD | 2 Wire Switch (NO) To JB
INS | ZAH | Road Drop Alarm High |  | DCS
INS | ZAHH | Road Drop Alarm High High |  | DCS
INS | ZE | Road Drop |  | FLD
INS | ZI | Road Drop Indicating |  | DCS
INS | ZT | Road Drop Transmitter | AI | FLD

## Powder_LIST
[13 empty] | INSTRUMENT INDEX FOR POWDER TRANSFER PACKAGE | [41 empty] | 향후 필요시 추가 고려 ---> only for IMPORT into AVEVA ( HOLD )
[9 empty] | PROJECT NO. : | 3944
[5 empty] | 아래 분리 TAG는 실제 입력 대상이고, 공식 출력물에서는 나타나지 않음 |  |  |  | MR NO. : | 0171 | [32 empty] | IO LIST용 추가 COLUMN (DB에 해당 FIELD 생성) | [11 empty] | Process data |  |  | Operating Condition | [11 empty] | Design Data
[9 empty] | DOC TITLE : | Instrument Index
[9 empty] | DOC NO. : | 3944-VD-0171-DYP-RE-400-INX-0080
[9 empty] | REV : | 0
[58 empty] | Flow |  |  |  | Temperature |  |  |  | Pressure |  |  |  | Design Pressure | Design Temp. | Diff. Pressure | Shutoff Pressure | Back Pressure (Total)
REV | PLANT | UNIT | LOOP NO | LOOP SEQ. NO | Unit | Function | Serial | Suffix | TAG NO. | P&ID No. | FLUID | FLUID STATUS | SERVICE | INST.TYPE | SCOPE | LOC. (From) | SYSTEM (To.) | IO TYPE | SYSTEM LOC. | EXT.POWER | CALIB. RANGE MIN | CALIB. RANGE MAX | CALIB. RANGE UNIT | SCALE RANGE MIN | SCALE RANGE MAX | SCALE RANGE UNIT | INST.SIZE (INLET) | INST.RATING (INLET) | INST.SIZE (OUTLET) | INST.RATING (OUTLET) | MATL.BODY | MATL.ELEM | VALVE FAIL | LINE SIZE | LINE SPEC | EQUIPT NO. | PKG NO. | ACC. | PO NO. | INSTRUMENT LOCATION LAYOUT DWG, | INSTRUMENT PIPING & TUBING HOOK-UP DWG. | REMARK | EXTER. POWER | IS/NIS | CONTACT STATUS | LOGIC No. | CONTROLLER ACTION | DCS RANGE MIN | DCS RANGE MAX | DCS RANGE UNIT | ALARM SP_LL | ALARM SP_L | ALARM SP_H | ALARM SP_HH | Specific Gravity | Viscosity | Molecular Weight | Min. | Nor. | Max | Unit | Min. | Nor. | Max | Unit | Min. | Nor. | Max | Unit
P&ID NO. : 20070
0 | 44 | 400 | [6 empty] | XV-2007001 | 20070 | - | - | 44TK-20001A SLIDE GATE VALVE | SLIDE GATE VALVE |  | FIELD
0 | 44 | 400 | [6 empty] | XVY-2007001A | 20070 | - | - | 44TK-20001A SOLENOID VALVE OPEN COMMAND | SOLENOID VALVE |  | FIELD | DCS | DO
0 | 44 | 400 | [6 empty] | XVY-2007001B | 20070 | - | - | 44TK-20001A SOLENOID VALVE CLOSE COMMAND | SOLENOID VALVE |  | FIELD | DCS | DO
0 | 44 | 400 | [6 empty] | ZSO-2007001 | 20070 | - | - | 44TK-20001A SLIDE GATE VALVE OPEN LIMIT SWITCH | LIMIT SWITCH |  | FIELD | DCS | DI
0 | 44 | 400 | [6 empty] | ZSC-2007001 | 20070 | - | - | 44TK-20001A SLIDE GATE VALVE CLOSE LIMIT SWITCH | LIMIT SWITCH |  | FIELD | DCS | DI
0 | 44 | 400 | [6 empty] | XV-2007003 | 20070 | - | - | 44PN-20002A SLIDE GATE VALVE | SLIDE GATE VALVE |  | FIELD
0 | 44 | 400 | [6 empty] | XVY-2007003A | 20070 | - | - | 44PN-20002A SOLENOID VALVE OPEN COMMAND | SOLENOID VALVE |  | FIELD | DCS | DO
0 | 44 | 400 | [6 empty] | XVY-2007003B | 20070 | - | - | 44PN-20002A SOLENOID VALVE CLOSE COMMAND | SOLENOID VALVE |  | FIELD | DCS | DO
0 | 44 | 400 | [6 empty] | ZSO-2007003 | 20070 | - | - | 44PN-20002A SLIDE GATE VALVE OPEN LIMIT SWITCH | LIMIT SWITCH |  | FIELD | DCS | DI
0 | 44 | 400 | [6 empty] | ZSC-2007003 | 20070 | - | - | 44PN-20002A SLIDE GATE VALVE CLOSE LIMIT SWITCH | LIMIT SWITCH |  | FIELD | DCS | DI
0 | 44 | 400 | [6 empty] | XV-2007019 | 20070 | - | - | 44PN-20002A BUTTERFLY VALVE | BUTTERFLY VALVE |  | FIELD
0 | 44 | 400 | [6 empty] | XVY-2007019A | 20070 | - | - | 44PN-20002A SOLENOID VALVE OPEN COMMAND | SOLENOID VALVE |  | FIELD | DCS | DO
0 | 44 | 400 | [6 empty] | XVY-2007019B | 20070 | - | - | 44PN-20002A SOLENOID VALVE CLOSE COMMAND | SOLENOID VALVE |  | FIELD | DCS | DO
0 | 44 | 400 | [6 empty] | ZSO-2007019 | 20070 | - | - | 44PN-20002A BUTTERFLY VALVE OPEN LIMIT SWITCH | LIMIT SWITCH |  | FIELD | DCS | DI
0 | 44 | 400 | [6 empty] | ZSC-2007019 | 20070 | - | - | 44PN-20002A BUTTERFLY VALVE CLOSE LIMIT SWITCH | LIMIT SWITCH |  | FIELD | DCS | DI
0 | 44 | 400 | [6 empty] | XVY-2007031B | 20070 | - | - | 44PN-20002A SOLENOID VALVE CLOSE COMMAND | SOLENOID VALVE |  | FIELD | DCS | DO
0 | 44 | 400 | [6 empty] | XV-2007002 | 20070 | - | - | 44TK-20001B SLIDE GATE VALVE | SLIDE GATE VALVE |  | FIELD
0 | 44 | 400 | [6 empty] | XVY-2007002A | 20070 | - | - | 44TK-20001B SOLENOID VALVE OPEN COMMAND | SOLENOID VALVE |  | FIELD | DCS | DO
0 | 44 | 400 | [6 empty] | XVY-2007002B | 20070 | - | - | 44TK-20001B SOLENOID VALVE CLOSE COMMAND | SOLENOID VALVE |  | FIELD | DCS | DO
0 | 44 | 400 | [6 empty] | ZSO-2007002 | 20070 | - | - | 44TK-20001B SLIDE GATE VALVE OPEN LIMIT SWITCH | LIMIT SWITCH |  | FIELD | DCS | DI
0 | 44 | 400 | [6 empty] | ZSC-2007002 | 20070 | - | - | 44TK-20001B SLIDE GATE VALVE CLOSE LIMIT SWITCH | LIMIT SWITCH |  | FIELD | DCS | DI
0 | 44 | 400 | [6 empty] | XV-2007004 | 20070 | - | - | 44PN-20002B SLIDE GATE VALVE | SLIDE GATE VALVE |  | FIELD
0 | 44 | 400 | [6 empty] | XVY-2007004A | 20070 | - | - | 44PN-20002B SOLENOID VALVE OPEN COMMAND | SOLENOID VALVE |  | FIELD | DCS | DO
0 | 44 | 400 | [6 empty] | XVY-2007004B | 20070 | - | - | 44PN-20002B SOLENOID VALVE CLOSE COMMAND | SOLENOID VALVE |  | FIELD | DCS | DO
0 | 44 | 400 | [6 empty] | ZSO-2007004 | 20070 | - | - | 44PN-20002B SLIDE GATE VALVE OPEN LIMIT SWITCH | LIMIT SWITCH |  | FIELD | DCS | DI
0 | 44 | 400 | [6 empty] | ZSC-2007004 | 20070 | - | - | 44PN-20002B SLIDE GATE VALVE CLOSE LIMIT SWITCH | LIMIT SWITCH |  | FIELD | DCS | DI
0 | 44 | 400 | [6 empty] | XV-2007020 | 20070 | - | - | 44PN-20002B BUTTERFLY VALVE | BUTTERFLY VALVE |  | FIELD
0 | 44 | 400 | [6 empty] | XVY-2007020A | 20070 | - | - | 44PN-20002B SOLENOID VALVE OPEN COMMAND | SOLENOID VALVE |  | FIELD | DCS | DO
0 | 44 | 400 | [6 empty] | XVY-2007020B | 20070 | - | - | 44PN-20002B SOLENOID VALVE CLOSE COMMAND | SOLENOID VALVE |  | FIELD | DCS | DO
0 | 44 | 400 | [6 empty] | ZSO-2007020 | 20070 | - | - | 44PN-20002B BUTTERFLY VALVE OPEN LIMIT SWITCH | LIMIT SWITCH |  | FIELD | DCS | DI
0 | 44 | 400 | [6 empty] | ZSC-2007020 | 20070 | - | - | 44PN-20002B BUTTERFLY VALVE CLOSE LIMIT SWITCH | LIMIT SWITCH |  | FIELD | DCS | DI
0 | 44 | 400 | [6 empty] | XVY-2007032B | 20070 | - | - | 44PN-20002B SOLENOID VALVE CLOSE COMMAND | SOLENOID VALVE |  | FIELD | DCS | DO
0 | 44 | 400 | [6 empty] | XV-2007005 | 20070 | - | - | 44PN-20002AX1 BUTTERFLY VALVE | BUTTERFLY VALVE |  | FIELD
0 | 44 | 400 | [6 empty] | XVY-2007005A | 20070 | - | - | 44PN-20002AX1 SOLENOID VALVE OPEN COMMAND | SOLENOID VALVE |  | FIELD | DCS | DO
0 | 44 | 400 | [6 empty] | XVY-2007005B | 20070 | - | - | 44PN-20002AX1 SOLENOID VALVE CLOSE COMMAND | SOLENOID VALVE |  | FIELD | DCS | DO
0 | 44 | 400 | [6 empty] | ZSO-2007005 | 20070 | - | - | 44PN-20002AX1 BUTTERFLY VALVE OPEN LIMIT SWITCH | LIMIT SWITCH |  | FIELD | DCS | DI
0 | 44 | 400 | [6 empty] | ZSC-2007005 | 20070 | - | - | 44PN-20002AX1 BUTTERFLY VALVE CLOSE LIMIT SWITCH | LIMIT SWITCH |  | FIELD | DCS | DI
0 | 44 | 400 | [6 empty] | PI-2007061 | 20070 | - | - | 44PN-20002AX1 PRESSURE GAUGE | PRESSURE GAUGE |  | FIELD
0 | 44 | 400 | [6 empty] | PT-2007062 | 20070 | - | - | 44PN-20002AX1 PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | FIELD | DCS | AI
0 | 44 | 400 | [6 empty] | HVY-2007020 | 20070 | - | - | 44F-20002 SOLENOID VALVE OPEN COMMAND | SOLENOID VALVE |  | FIELD | DCS | DO
0 | 44 | 400 | [6 empty] | PI-2007064 | 20070 | - | - | 44F-20002 PRESSURE GAUGE | PRESSURE GAUGE |  | FIELD
0 | 44 | 400 | [6 empty] | PDIS-2007003 | 20070 | - | - | 44F-20002 DIFF. PRESSURE TRANSMITTER | DIFF. PRESSURE TRANSMITTER |  | FIELD | DCS | AI
0 | 44 | 400 | [6 empty] | XV-2007001 | 20070 | - | - | 44F-20002 BALL VALVE | BALL VALVE |  | FIELD
0 | 44 | 400 | [6 empty] | XVY-2007001A | 20070 | - | - | 44F-20002 SOLENOID VALVE OPEN COMMAND | SOLENOID VALVE |  | FIELD | DCS | DO
0 | 44 | 400 | [6 empty] | XVY-2007001B | 20070 | - | - | 44F-20002 SOLENOID VALVE CLOSE COMMAND | SOLENOID VALVE |  | FIELD | DCS | DO
0 | 44 | 400 | [6 empty] | ZSO-2007001 | 20070 | - | - | 44F-20002 BALL VALVE OPEN LIMIT SWITCH | LIMIT SWITCH |  | FIELD | DCS | DI
0 | 44 | 400 | [6 empty] | ZSC-2007001 | 20070 | - | - | 44F-20002 BALL VALVE CLOSE LIMIT SWITCH | LIMIT SWITCH |  | FIELD | DCS | DI
0 | 44 | 400 | [6 empty] | XV-2007002 | 20070 | - | - | 44F-20002 BALL VALVE | BALL VALVE |  | FIELD
0 | 44 | 400 | [6 empty] | XVY-2007002A | 20070 | - | - | 44F-20002 SOLENOID VALVE OPEN COMMAND | SOLENOID VALVE |  | FIELD | DCS | DO
0 | 44 | 400 | [6 empty] | XVY-2007002B | 20070 | - | - | 44F-20002 SOLENOID VALVE CLOSE COMMAND | SOLENOID VALVE |  | FIELD | DCS | DO
0 | 44 | 400 | [6 empty] | ZSO-2007002 | 20070 | - | - | 44F-20002 BALL VALVE OPEN LIMIT SWITCH | LIMIT SWITCH |  | FIELD | DCS | DI
0 | 44 | 400 | [6 empty] | ZSC-2007002 | 20070 | - | - | 44F-20002 BALL VALVE CLOSE LIMIT SWITCH | LIMIT SWITCH |  | FIELD | DCS | DI
0 | 44 | 400 | [6 empty] | XV-2007003 | 20070 | - | - | 44F-20002 BALL VALVE | BALL VALVE |  | FIELD
0 | 44 | 400 | [6 empty] | XVY-2007003A | 20070 | - | - | 44F-20002 SOLENOID VALVE OPEN COMMAND | SOLENOID VALVE |  | FIELD | DCS | DO
0 | 44 | 400 | [6 empty] | XVY-2007003B | 20070 | - | - | 44F-20002 SOLENOID VALVE CLOSE COMMAND | SOLENOID VALVE |  | FIELD | DCS | DO
0 | 44 | 400 | [6 empty] | ZSO-2007003 | 20070 | - | - | 44F-20002 BALL VALVE OPEN LIMIT SWITCH | LIMIT SWITCH |  | FIELD | DCS | DI
0 | 44 | 400 | [6 empty] | ZSC-2007003 | 20070 | - | - | 44F-20002 BALL VALVE CLOSE LIMIT SWITCH | LIMIT SWITCH |  | FIELD | DCS | DI
0 | 44 | 400 | [6 empty] | PCV-2007054 | 20070 | - | - | 44V-20001A PRESSURE CONTROL VALVE | PRESSURE CONTROL VALVE |  | FIELD
0 | 44 | 400 | [6 empty] | PI-2007055 | 20070 | - | - | 44V-20001A PRESSURE GAUGE | PRESSURE GAUGE |  | FIELD
0 | 44 | 400 | [6 empty] | XV-2007007 | 20070 | - | - | 44V-20001A BALL VALVE | BALL VALVE |  | FIELD
0 | 44 | 400 | [6 empty] | XVY-2007007A | 20070 | - | - | 44V-20001A SOLENOID VALVE OPEN COMMAND | SOLENOID VALVE |  | FIELD | DCS | DO
0 | 44 | 400 | [6 empty] | XVY-2007007B | 20070 | - | - | 44V-20001A SOLENOID VALVE CLOSE COMMAND | SOLENOID VALVE |  | FIELD | DCS | DO
0 | 44 | 400 | [6 empty] | ZSO-2007007 | 20070 | - | - | 44V-20001A BALL VALVE OPEN LIMIT SWITCH | LIMIT SWITCH |  | FIELD | DCS | DI
0 | 44 | 400 | [6 empty] | ZSC-2007007 | 20070 | - | - | 44V-20001A BALL VALVE CLOSE LIMIT SWITCH | LIMIT SWITCH |  | FIELD | DCS | DI
0 | 44 | 400 | [6 empty] | PT-2007006 | 20070 | - | - | 44V-20001A PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | FIELD | DCS | AI
0 | 44 | 400 | [6 empty] | PT-2007007 | 20070 | - | - | 44V-20001A PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | FIELD | DCS | AI
0 | 44 | 400 | [6 empty] | XV-2007008 | 20070 | - | - | 44V-20001A BALL VALVE | BALL VALVE |  | FIELD
0 | 44 | 400 | [6 empty] | XVY-2007008A | 20070 | - | - | 44V-20001A SOLENOID VALVE OPEN COMMAND | SOLENOID VALVE |  | FIELD | DCS | DO
0 | 44 | 400 | [6 empty] | XVY-2007008B | 20070 | - | - | 44V-20001A SOLENOID VALVE CLOSE COMMAND | SOLENOID VALVE |  | FIELD | DCS | DO
0 | 44 | 400 | [6 empty] | ZSO-2007008 | 20070 | - | - | 44V-20001A BALL VALVE OPEN LIMIT SWITCH | LIMIT SWITCH |  | FIELD | DCS | DI
0 | 44 | 400 | [6 empty] | ZSC-2007008 | 20070 | - | - | 44V-20001A BALL VALVE CLOSE LIMIT SWITCH | LIMIT SWITCH |  | FIELD | DCS | DI
0 | 44 | 400 | [6 empty] | XV-2007004 | 20070 | - | - | 44V-20001B BALL VALVE | BALL VALVE |  | FIELD
0 | 44 | 400 | [6 empty] | XVY-2007004A | 20070 | - | - | 44V-20001B SOLENOID VALVE OPEN COMMAND | SOLENOID VALVE |  | FIELD | DCS | DO
0 | 44 | 400 | [6 empty] | XVY-2007004B | 20070 | - | - | 44V-20001B SOLENOID VALVE CLOSE COMMAND | SOLENOID VALVE |  | FIELD | DCS | DO
0 | 44 | 400 | [6 empty] | ZSO-2007004 | 20070 | - | - | 44V-20001B BALL VALVE OPEN LIMIT SWITCH | LIMIT SWITCH |  | FIELD | DCS | DI
0 | 44 | 400 | [6 empty] | ZSC-2007004 | 20070 | - | - | 44V-20001B BALL VALVE CLOSE LIMIT SWITCH | LIMIT SWITCH |  | FIELD | DCS | DI
0 | 44 | 400 | [6 empty] | PT-2007006B | 20070 | - | - | 44V-20001B PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | FIELD | DCS | AI
0 | 44 | 400 | [6 empty] | PCV-2007055 | 20070 | - | - | 44V-20001B PRESSURE CONTROL VALVE | PRESSURE CONTROL VALVE |  | FIELD
0 | 44 | 400 | [6 empty] | PI-2007056 | 20070 | - | - | 44V-20001B PRESSURE GAUGE | PRESSURE GAUGE |  | FIELD
0 | 44 | 400 | [6 empty] | XV-2007009 | 20070 | - | - | 44V-20001B BALL VALVE | BALL VALVE |  | FIELD
0 | 44 | 400 | [6 empty] | XVY-2007009A | 20070 | - | - | 44V-20001B SOLENOID VALVE OPEN COMMAND | SOLENOID VALVE |  | FIELD | DCS | DO
0 | 44 | 400 | [6 empty] | XVY-2007009B | 20070 | - | - | 44V-20001B SOLENOID VALVE CLOSE COMMAND | SOLENOID VALVE |  | FIELD | DCS | DO
0 | 44 | 400 | [6 empty] | ZSO-2007009 | 20070 | - | - | 44V-20001B BALL VALVE OPEN LIMIT SWITCH | LIMIT SWITCH |  | FIELD | DCS | DI
0 | 44 | 400 | [6 empty] | ZSC-2007009 | 20070 | - | - | 44V-20001B BALL VALVE CLOSE LIMIT SWITCH | LIMIT SWITCH |  | FIELD | DCS | DI
0 | 44 | 400 | [6 empty] | XV-2007011 | 20070 | - | - | 44V-20001B BALL VALVE | BALL VALVE |  | FIELD
0 | 44 | 400 | [6 empty] | XVY-2007011A | 20070 | - | - | 44V-20001B SOLENOID VALVE OPEN COMMAND | SOLENOID VALVE |  | FIELD | DCS | DO
0 | 44 | 400 | [6 empty] | XVY-2007011B | 20070 | - | - | 44V-20001B SOLENOID VALVE CLOSE COMMAND | SOLENOID VALVE |  | FIELD | DCS | DO
0 | 44 | 400 | [6 empty] | ZSO-2007011 | 20070 | - | - | 44V-20001B BALL VALVE OPEN LIMIT SWITCH | LIMIT SWITCH |  | FIELD | DCS | DI
0 | 44 | 400 | [6 empty] | ZSC-2007011 | 20070 | - | - | 44V-20001B BALL VALVE CLOSE LIMIT SWITCH | LIMIT SWITCH |  | FIELD | DCS | DI
0 | 44 | 400 | [6 empty] | XV-2007005 | 20070 | - | - | 44V-20001B BALL VALVE | BALL VALVE |  | FIELD
0 | 44 | 400 | [6 empty] | XVY-2007005A | 20070 | - | - | 44V-20001B SOLENOID VALVE OPEN COMMAND | SOLENOID VALVE |  | FIELD | DCS | DO
0 | 44 | 400 | [6 empty] | XVY-2007005B | 20070 | - | - | 44V-20001B SOLENOID VALVE CLOSE COMMAND | SOLENOID VALVE |  | FIELD | DCS | DO
0 | 44 | 400 | [6 empty] | ZSO-2007005 | 20070 | - | - | 44V-20001B BALL VALVE OPEN LIMIT SWITCH | LIMIT SWITCH |  | FIELD | DCS | DI
0 | 44 | 400 | [6 empty] | ZSC-2007005 | 20070 | - | - | 44V-20001B BALL VALVE CLOSE LIMIT SWITCH | LIMIT SWITCH |  | FIELD | DCS | DI
0 | 44 | 400 | [6 empty] | XV-2007006 | 20070 | - | - | 44V-20001B BALL VALVE | BALL VALVE |  | FIELD
0 | 44 | 400 | [6 empty] | XVY-2007006A | 20070 | - | - | 44V-20001B SOLENOID VALVE OPEN COMMAND | SOLENOID VALVE |  | FIELD | DCS | DO
0 | 44 | 400 | [6 empty] | XVY-2007006B | 20070 | - | - | 44V-20001B SOLENOID VALVE CLOSE COMMAND | SOLENOID VALVE |  | FIELD | DCS | DO
0 | 44 | 400 | [6 empty] | ZSO-2007006 | 20070 | - | - | 44V-20001B BALL VALVE OPEN LIMIT SWITCH | LIMIT SWITCH |  | FIELD | DCS | DI
0 | 44 | 400 | [6 empty] | ZSC-2007006 | 20070 | - | - | 44V-20001B BALL VALVE CLOSE LIMIT SWITCH | LIMIT SWITCH |  | FIELD | DCS | DI
0 | 44 | 400 | [6 empty] | XV-2007010 | 20070 | - | - | 44V-20001B BALL VALVE | BALL VALVE |  | FIELD
0 | 44 | 400 | [6 empty] | XVY-2007010A | 20070 | - | - | 44V-20001B SOLENOID VALVE OPEN COMMAND | SOLENOID VALVE |  | FIELD | DCS | DO
0 | 44 | 400 | [6 empty] | XVY-2007010B | 20070 | - | - | 44V-20001B SOLENOID VALVE CLOSE COMMAND | SOLENOID VALVE |  | FIELD | DCS | DO
0 | 44 | 400 | [6 empty] | ZSO-2007010 | 20070 | - | - | 44V-20001B BALL VALVE OPEN LIMIT SWITCH | LIMIT SWITCH |  | FIELD | DCS | DI
0 | 44 | 400 | [6 empty] | ZSC-2007010 | 20070 | - | - | 44V-20001B BALL VALVE CLOSE LIMIT SWITCH | LIMIT SWITCH |  | FIELD | DCS | DI
0 | 44 | 400 | [6 empty] | PT-2007004 | 20070 | - | - | 44V-20001B PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | FIELD | DCS | AI
0 | 44 | 400 | [6 empty] | PT-2007005 | 20070 | - | - | 44V-20001B PRESSURE TRANSMITTER | PRESSURE TRANSMITTER |  | FIELD | DCS | AI

## Pellet_LIST
[13 empty] | INSTRUMENT INDEX FOR PELLET TRANSFER PACKAGE | [41 empty] | 향후 필요시 추가 고려 ---> only for IMPORT into AVEVA ( HOLD )
PROJECT NO. :
[5 empty] | 아래 분리 TAG는 실제 입력 대상이고, 공식 출력물에서는 나타나지 않음 |  |  |  | JOB NO. : | [33 empty] | IO LIST용 추가 COLUMN (DB에 해당 FIELD 생성) | [11 empty] | Process data |  |  | Operating Condition | [11 empty] | Design Data
DOC TITLE :
DOC NO. :
REV :
[58 empty] | Flow |  |  |  | Temperature |  |  |  | Pressure |  |  |  | Design Pressure | Design Temp. | Diff. Pressure | Shutoff Pressure | Back Pressure (Total)
REV | PLANT | UNIT | LOOP NO | LOOP SEQ. NO | Unit | Function | Serial | Suffix | TAG NO. | P&ID No. | FLUID | FLUID STATUS | SERVICE | INST.TYPE | SCOPE | LOC. (From) | SYSTEM (To.) | IO TYPE | SYSTEM LOC. | EXT.POWER | CALIB. RANGE MIN | CALIB. RANGE MAX | CALIB. RANGE UNIT | SCALE RANGE MIN | SCALE RANGE MAX | SCALE RANGE UNIT | INST.SIZE (INLET) | INST.RATING (INLET) | INST.SIZE (OUTLET) | INST.RATING (OUTLET) | MATL.BODY | MATL.ELEM | VALVE FAIL | LINE SIZE | LINE SPEC | EQUIPT NO. | PKG NO. | ACC. | PO NO. | INSTRUMENT LOCATION LAYOUT DWG, | INSTRUMENT PIPING & TUBING HOOK-UP DWG. | REMARK | EXTER. POWER | IS/NIS | CONTACT STATUS | LOGIC No. | CONTROLLER ACTION | DCS RANGE MIN | DCS RANGE MAX | DCS RANGE UNIT | ALARM SP_LL | ALARM SP_L | ALARM SP_H | ALARM SP_HH | Specific Gravity | Viscosity | Molecular Weight | Min. | Nor. | Max | Unit | Min. | Nor. | Max | Unit | Min. | Nor. | Max | Unit