Dear Mr. Bahramian,

I would like to remind you that, per standards, using 150# for the cooling water inlet and outlet is fully acceptable. We have not received any specifications or PO documents requiring 300# for piping below 2”.

Please note that upgrading to 300# would require redesigning the compressor, which will delay delivery of key components. To avoid this, I recommend keeping the current 150# design.

Alternatively, we can change only the inlet and outlet flanges to 300#, allowing for 300# external piping, while maintaining 150# internally. This can be implemented without delay.

Kindly confirm your preferred option:

- Upgrade full cooling water system to 300# (with delay) X

- Change flanges to 300#, keep internals at 150# (no delay) (CONFIRM)

- Keep current 150# design as per latest P&ID X

Looking forward to your response.